- Revision History

| Rev.No. | Details of changes | Reason for change |
| --- | --- | --- |
| 01 | NA | Periodic Review |
| 02 | Specification of the magnehelic gauge limit of LAF. | Due to magnehelic gauge limit of LAF was not Specified in old SOP’S. |

2.0    Objective

To lay down a procedure for operation and cleaning of Ceiling Mounted Laminar Air Flow    Devices.

3.0    Scopes

This SOP is applicable for operation and cleaning of Ceiling Mounted Laminar Air Flow Devices in vial washing and aseptic area of C Block.

# 4.0	Responsibility

Officer and Above Production	:	Implemented the Procedure.

5.0	   Accountability

Production Head.

- Procedure

6.1  Operation

6.1.1 Check the area and surrounding shall be clean.

6.1.2 Switch ON the red button for starting of the Ceiling Mounted Laminar airflow blower.

6.1.3 Switch ON the red button for tube light.

6.1.4 Check the pressure differential should be within limits (8 to 15 mm of WC) as mentioned below the magnehelic gauges.

6.1.5 If the reading is more than the limit it indicates the HEPA filters are chocked.

6.1.6 If the pressure reading is lower than the limit it indicates the HEPA filter integrity is lost.

6.1.7 If problem observed inform to Engg. Department for corrective actions and Put the under maintenance tag on the machine.

6.1.8 Ceiling Mounted Laminar airflow to be started at least half an hour before starting up of any activities.

6.1.9 When the respective activity is over switch OFF the blowers and tube lights of Ceiling Mounted Laminar air flow.

6.2	   Cleaning Procedure

6.2.1 After all the activities over, Switch OFF the Red button to switch OFF the blower.

6.2.2 Clean the Ceiling Mounted LAF by lint free duster.

6.2.3 Mop the Ceiling Mounted LAF using freshly prepared 70% IPA.

6.2.4 Switch off the tube light after cleaning is over.

6.2.5 Affix the CLEANED label.

7.0    Annexure (S)

NA

8.0   Reference (S)

NA

9.0    Glossary

SOP		: Standard Operating Procedure

LAF		: Laminar air flow

IPA		: Iso-propyl Alcohol

Mm of wc	: millimeter of water column

HEPA 		: High efficiency particulate air filter