- Revision History

| Rev.No. | Details of changes | Reason for change |
| --- | --- | --- |
| 01 | NA | Periodic Review |
| 02 | NA | Periodic Review |

2.0    Objective

To lay down a procedure for operation and cleaning of Mobile Laminar Air Flow Devices and Pre-filters.

3.0    Scopes

This SOP is applicable for operation and cleaning of Mobile Laminar Air Flow Devices and Pre- filters in aseptic area of C Block.

# 4.0	Responsibility

Technician			: 	Operation and Cleaning.

Officer and Above Production	:	Implemented the Procedure.

5.0	   Accountability

Production Head.

6.0    Procedure

  - Operation

6.1.1 Check the area and surrounding shall be clean.

6.1.2 Switch ON the red button for starting of the Mobile Laminar airflow blower.

6.1.3 Switch ON the red button for U.V. light.

6.1.4 Check the pressure differential should be within limits (8 to 15 mm of wc) as mentioned below   the magnehelic gauges.

6.1.5 If the reading is more than the limit it indicates the HEPA filters are chocked.

6.1.6 If the pressure reading is lower than the limit it indicates the HEPA filter integrity is lost.

6.1.7 If problem observed inform to Engg. Department for corrective actions and Put the UNDER MAINTAINANCE tag on the machine.

6.1.8 Mobile Laminar airflow Devices must be ON continuously.

6.2	    Cleaning Procedure of Mobile Laminar Air Flow.

6.2.1   After all the activities are over, Switch OFF the Red button to switch OFF the blower.

6.2.2   Clean the Mobile LAF by lint free duster.

6.2.3   Mop the LAF using freshly prepared 70% IPA.

6.2.4   Switch ON the U.V. light after cleaning is over.

6.2.5   Affix the CLEANED label.

6.3     Cleaning Procedures of Pre-filters.

- Switch OFF the laminar airflow device.

- Remove all the pre filters from Laminar Air Flow devices.

- Send the pre-filter through change room to washing area of respective vial line in poly bags.

- Remove one filter at a time from the poly bag. Check the filters for any damage, if damage found inform immediately to Production or Engineering Officer / Executive to change the filter.

- Wash the pre filters with purified water in the manner that the direction of purified water shall run in reverse direction to that of airflows. Repeat the step 3-4 times till there are no remnants of the product in the pre filters. Visually check that there are no remnants of the product.

- Rinse the pre filters again with water for injection in the manner that the direction of water for injection shall run in reverse direction to that of airflow.

- Air-dry the Pre-filters.

- Wrap the filter in the pre sanitized poly bags.

- Transfer the filters to aseptic area through change room of the aseptic area. Take out the filters from the poly bags and discard the poly bag in change room I st in waste bin.

- Sanitize the filters using fogger before taking it to the respective area.

- Use hospital trolley to transfer the filters to the respective area.

- Fix the filters in the respective LAF devices and fit the grills.

- When all the LAF Pre filters and returned air risers are fitted to there respective grills, then area shall be fumigated before startup of routine activity in aseptic area.

- Filter cleaning shall be done fortnightly or as and when required. Entries shall be made in the cleaning record.

7.0      Annexure (S)

Annexure –I: Cleaning Record of Pre-filter.

8.0      Reference (S)

NA

9.0      Glossary

SOP		: Standard Operating Procedure.

LAF		: Laminar air flow.

IPA		: Iso-propyl Alcohol