- Objective

To lay down a procedure for pressure differential monitoring record.

- Scope

This SOP is applicable for recording the pressure differential in Production Areas of Alkem Laboratory Ltd. Unit-II, Baddi.

- Responsibility:

Production Officer/Executive

Production technician

- Accountability:

Head Production

- Procedure:

  - Ensure that the door of the room under observation is closed properly.

  - Observe the Magnehelic gauge reading.

  - The reading of magnehelic gauge shall not be less than 4 Pascal.

  - If the gauge is showing pressure beyond the limit, inform maintenance department for corrective action.

  - Record the pressure differential in FORMAT NO.xxx in Annexure-I

  - Record the pressure differential at the start of the operation and at every four hours interval.

  - cleaning procedure:

    - Dry mop the instrument with lint free cloth.

    - Cleaned both side tubes ends, once in a week.

- Enclosures:

Annexure-I Environmental Condition and Pressure Differential Record.

Change History Log

SOP Training Record

- Abbreviations:

SOP:  Standard Operating Procedure

No. :  Number

- Revision history

| Revision No. | Details Of Changes | Reason for Change |
| --- | --- | --- |
| 00 | New SOP |  |