- Revision History

| Rev.No. | Details of changes | Reason for change |
| --- | --- | --- |
| 01 | NA | Periodic Review |
| 02 | Increase hold time study of Sterilized garments. | Due to change hold time study from 48 hours to 72 hours of garments. |

2.0    Objective

To lay down a procedure for operation and cleaning of garment cubicle.

# 3.0    Scopes

# This SOP is applicable for operation and cleaning of garment cubicle for aseptic area in C Block.

4.0	   Responsibility

Technician			:	Operation and cleaning.

Officer and Above Production	:	Implementation of Procedure.

5.0	   Accountability

Production Head.

  - Procedure

  - Pre-Start Up

    - Ensure that the power cord is connected to the main supply.

6.1.2	Ensure that door of the garment cubicle is closed.

6.1.3 	Ensure that UV light and blower of the garment cubicle are in working condition.

    - Ensure that IR lamp of the garment cubicle is in working condition.

6.2	Start Up

- Switch ON the MAIN.

- Switch on the blower of the garment cubicle. The reading in maghenelic gauge should be within the specified limit (8 to 15 mm of water).

- Switch off the UV light then open the door of the garment cubicle.

- Mop the shelf of the garment cubicle with the help of sterile mop using freshly prepared & filtered 70%IPA (use within 72hrs).

- Place the sterilized garment and gloves on the shelf provided in garment cubicle.

- Place the booties on the lower shelf in the cubicle.

- Close the door and switch ON the UV light and IR lamp.

- To take the garment from the garment cubicle switch OFF the UV light then open the door of the cubicle take one set of the garment then close the door. Switch ON the UV light.

6.3	 Cleaning Procedure

- Switch off the MAIN.

- At the end of the working day remove the remaining garment from the garment cubicle send them to washing area.

- Clean the garment cubicle with filtered 70% IPA solution followed by outer side using sterile lint free mop.

- After cleaning operation is over switch ON the mains then blower followed by UV light and IR lamp.

7.0      Annexure (S)

NA

8.0       Reference (S)

NA

9.0	Glossary

SOP		   : Standard Operating Procedure.

LAF	   : Laminar airflow.

IPA	   : Isopropyl Alcohol

UV	   : Ultra violet

IR	   : Infra red

WFI	   : Water for injection

PC	   : Production (C-Block)