- Revision History

| Rev.No. | Details of changes | Reason for change |
| --- | --- | --- |
| 01 | NA | Periodic Review |

2.0    Objective

To lay down procedure for use of filters and silicone tubes.

# 3.0    Scopes

This SOP is applicable for use of filters and silicone tubes in the production area.

# 4.0	Responsibility

Officer and Above Production	:	Implementation of Procedure.

5.0	   Accountability

Production Head.

- Procedure

# The filters and silicone tubes shall be used as per schedule given below the table, after Use, it 	         shall be send to scrap yard.

| S. No. | Type of Items | Location | Integrity |  | Usage |
| --- | --- | --- | --- | --- | --- |
|  |  |  | Pre | Post |  |
| 1.0 | Disinfectant filter | --- | Before Sterilization | After Filtration | Disinfectant dedicated |
| 2.0 | Hydrophobic(Air) filter( 0.2µ) | Compressed air /Nitrogen line/oxygen/carbon dioxide line filters | Every 30 days |  | 12 months or when integrity fails whicever is earlier |
| 3.0 | Hydrophobic(Vent) filter( 0.2µ) | Steam Sterilizer/Terminal Sterilizer | Every 30 days |  | 12 months or when integrity fails whicever is earlier |
| 4.0 | Silicone tube | WFI collection | ------------ |  | NMT 3 Months/ When ever Color changes which ever is earlier |
| 5.0 | Silicone tube | Disinfectant filtration | ------------ |  | NMT 3 Months/ When ever Color changes which ever is earlier |
| 6.0 | Hydrophillic Filter (5.0µ) | Purified Water | ------------ |  | 12 months or when integrity fails whicever is earlier |
| # 7.0 | Hydrophilliic Filter (5.0µ) | WFI | ------------ |  | 12 months or when integrity fails whicever is earlier |
| # 8.0 | Hydrophillic Filter (10.0µ) | Re circuleted Water | ------------- |  | NMT 1 Months/ When ever Color changes whichever is earlier |

7.0      Annexure (S)

Annexure- I: Filter Installation / Replacement Record.

8.0     Reference (S)

NA

9.0     Glossary

SOP      	: Standard Operating Procedure.

WFI		: Water for Injection

NO              : Number

PC		: Production C-Block