USER REQUIREMENT SPECIFICATION

TABLE OF CONTENTS

| Sr. No | Contents | Page No |
| --- | --- | --- |
| A | Approval Signature | 04 |
| B | Revision History | 05 |
| C | Objective | 06 |
| 1.0 | Basis of Design | 07 |
| 1.1 | Name Of The Equipment | 07 |
| 1.2 | Use Of The Equipment | 07 |
| 1.3 | Mode Of Action | 07 |
| 1.4 | Input Used And Output Produced | 07 |
| 1.4.1 | Input Used | 07 |
| 1.4.2 | Output Produced | 07 |
| 1.5 | Process Description | 08 |
| 1.5.1 | Process | 08 |
| 1.5.2 | Discharging Of Output | 08 |
| 1.6 | Total Operation Time Per Day | 09 |
| 1.7 | Operator Involvement | 09 |
| 1.8 | Effect On Environment | 09 |
| 1.9 | Environment of Installation | 09 |
| 1.9.1 | Allocated Floor Space | 09 |
| 1.9.2 | Vertical Clearance | 09 |
| 1.9.3 | Physical Clearance | 09 |
| 2.0 | Structural Design Requirement | 10 |
| 2.1 | Material Of Construction And Surface Finish | 10 |
| 2.2 | Identified Critical Components | 10 |
| 2.3 | Utility Requirement | 10 |
| 2.4 | Design Features For Validation (If Any) | 11 |
| 3.0 | Functional Requirement | 11 |
| 3.1 | Process Control | 11 |
| 3.2 | Design Features | 11 |
| 3.3 | Design Features Based On Safety | 11 |
| 3.3.1 | Process Safety | 11 |
| 3.3.2 | Operator and Environmental Safety | 11 |
| 3.4 | Cleaning Requirement | 11 |
| 3.5 | Emergency Stop | 11 |
| 3.6 | Alarms And Warning | 12 |
| 3.7 | Power Failure And Restart Requirement | 12 |
| 4.0 | Containment | 12 |
| 4.1 | Explosion Protection | 12 |
| 4.2 | Containment Of The Product | 12 |
| 5.0 | Support required from supplier | 12 |
| 5.1 | Pre-Installation Support | 12 |
| 5.2 | Start-Up Support | 12 |
| 5.3 | Documentation | 13 |
| 6.0 | Performance Specification | 13 |
| 7.0 | Validation Requirement | 13 |

##### A)	APPROVAL SIGNATURE

Signing of this Approval page indicates agreement with the User Requirement Specification described in this document. Should Modifications to the User Requirement Specification become necessary, an addendum will be prepared and approved.

Prepared By:

| Functional Area | Name | Signature | Date |
| --- | --- | --- | --- |
| ###### E Engineering |  |  |  |

Reviewed By:

| Functional Area | Name | Signature | Date |
| --- | --- | --- | --- |
| ###### Head Engineering |  |  |  |
| ###### H Head Production |  |  |  |
| ###### Head Validation |  |  |  |

Approved By:

| ###### Head Operation |  |  |  |
| --- | --- | --- | --- |
| ###### Head QA |  |  |  |

## B)	REVISION HISTORY:-

| REVISION NO | DATE | REVISION DESCRIPTION |
| --- | --- | --- |

- C)	OBJECTIVE

This document contains the specification, called as User Requirement Specification, required as a basis of designing HVAC system to be purchased / fabricated from any external agency. The competent staff of Alkem laboratories limited, who are trained or experienced on the process and regulatory requirements, approves this specification. This User Requirement Specification is prepared to document the expectation of Alkem Laboratories Limited from suppliers of the system, which should be suitable to the process and regulatory requirement and to comply the performance criteria established by   Alkem Laboratories Limited.

- BASIS OF DESIGN

- Name of the Equipment

AIR HANDLING UNIT (AHU)

- Use of the Equipment

The System is used to supply clean and conditioned air to all the process controlled areas to maintain cleanliness, positive pressure, temperature and relative humidity in the area, as per process/product requirements.

- Mode of Action

System passes the air through several stages of filtration to clean the air upto required standard and then passes it through cooling or heating coil to attain the required temperature and relative humidity level. System supplies sufficient and controlled amount of air to maintain the desired pressure. System replaces air inside the controlled process rooms with sufficient amount of clean and conditioned air.

- Input used and output produced. Mention the physical property of inputs / outputs which will be suitable for engineering design of equipment. Mention specifically if any input / in-process material / finished product may hamper the equipment or any product quality may be affected by the equipment.

- Input used:

Load articles: - Untreated fresh air. - Return air from the process areas. - Chilled water ( NMT 7OC) to cool down the air. - Hot water at (NLT 45c) to reduce the RH level of the air. - 3 phase electrical supply with 440 v & 50 Hz

- Output Produced

Clean filtered air at required pressure differential, temperature and RH level. User definition of environmental parameters of different process areas are given in Annexure # 01

- Process Description

- Process (Preferably demonstrate with flow chart)

- Fresh air (10 to 20% of total achieved cfm, EU-4, 10 )

- Filtering of air with Pre Filters.( EU –4, 10 )

- Cooling of air with chilled water circulating in cooling coil.

- Heating of air, if required with hot water circulating in heating coil.

- Filtering of air with Fine/Intermediate Filters.( EU – 6, 5)

- Filtering of air with High Efficiency Particulate Airborne (HEPA, EU-13) filter (Terminal / Plenum), if required. (Grade-D)

- Suction of air through return risers (20, EU-3) from the process area

- Air is exhausted to atmosphere through after filtration wherever required.

- In the mixing chamber, return air and fresh air get mixed

- . Process repeats from `b’.

Remarks: The step d), f), g) and h) are optional, as per the requirement.

- Discharging of output

Clean filtered air with required temperature and RH level will enter the room through supply air grills / diffuser / HEPA filter and before going to return.(Details in Annexure # 01

- Total operation time per day

Design for round O clock

- Operator involvement

- Preventive Maintenance (cleaning of filters, cleaning of AHU inner cabinet etc.) - Manual valve operation.

- Effect on environment

System should not release toxic and hazardous substances directly to the atmosphere. All the substances and particles should get arrested through filteration releasing exhaust air to the atmosphere.

| - Environment Of Installation |  |
| --- | --- |
| - Allocated floor space with allocated corridor |  |
| There must be enough space for routine preventive and break down maintenance around the equipment at service floor. |  |
| - Vertical clearance |  |
| Vertical clearance should allow the routine preventive and break down maintenance of equipment. |  |
| - Physical Condition |  |
| Room Temperature | Ambient |
| Relative Humidity | Ambient |
| Cleanliness | Atmospheric condition |

| - STRUCTURAL DESIGN REQUIREMENT |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| - Material of Construction and surface finish of critical and contact parts |  |  |  |  |  |  |  |
| Contact parts with process air (metallic) like ducting and AHU inner periphery etc. |  |  |  | Galvanized iron, Aluminum or Stainless Steel |  |  |  |
| Non-contact parts with process air (metallic) like AHU outer periphery and nut bolts etc. |  |  |  | Galvanized iron or Aluminum |  |  |  |
| Gasket for ducting |  |  |  | Neoprene |  |  |  |
| Surface Finish |  |  |  | Insulated with Aluminum cladding in case of GI. |  |  |  |
| - Identified critical component (write with purpose, scope of supply and characteristics suitable to comply the GMP requirements) |  |  |  |  |  |  |  |
| ### Component |  | Name and particulars of the component |  |  |  | Scope of the supply |  |
| Air supply equipment |  | Air Handling Unit |  |  |  | Supplier |  |
| Air cooling & heating system |  | Cooling and heating coil, in-built with Air Handling Unit |  |  |  | ##### Supplier |  |
| Air distribution network |  | Duct work, Damper & Filters |  |  |  | Supplier |  |
| Air filtration system |  | Pre, Fine and HEPA Filters |  |  |  | Supplier |  |
| - Utility requirement and availability of utility |  |  |  |  |  |  |  |
| Utility Name | Specification |  | Purpose |  | Scope of supply |  | Supply location |
| Electricity | Voltage:415V Phase: 3 Frequency: 50 Hz |  | For power to Air Handling Units and Dehumidifier |  | ##### User |  | ##### MCC Panel |
| Chilled Water | Temp. : NMT 7oC |  | For cooling action at cooling coil |  | ##### User |  | ##### AHU at Service Floor |
| Hot Water | Temp : NLT45 oC |  | For heating action at heating coil |  | ##### User |  | ##### AHU at Service Floor |

- Design features for validation (if any)

The system should consist of Differential Pressure gauge, Temperature gauge, and DOP Ports for periodic validation.

| - FUNCTIONAL REQUIREMENT |  |
| --- | --- |
| - Process control: |  |
| Air Handling Unit to be controlled for intake and discharge of air volumes |  |
| - Design features: |  |
| Design Specification |  |
| - Design Features based on safety |  |
| - Process safety( GMP) |  |
| - To control the Temperature, RH and P between the rooms within the specified limit and indicate out of limit condition GMP Requirements.(Annexure-1) |  |
| - Operator and environmental safety |  |
| Type of safety | ### Specification |
| Electrical Earthing | ##### Required |
| Scrubber system | Required for zero emission |
| Dust extractor | Required for the areas where Dust generation involved |
| Fire Damper | Fusible link damper |
| Noise level | It should not be more than 80Db( factory act) |
| - Cleaning requirement |  |
| Main components of the system shall be cleaned in place manually with water and air. Filters and coils (cooling coil and heating coil) shall be cleaned |  |
| 3.5 Emergency stop |  |
| The system shall have an E-Stop (stay put) string designed to stop all physical movement / operation of the machinery immediately. The E-Stop buttons shall be located in easily accessible areas around the machine. |  |
| - Alarms and warning |  |
| - In core area all AHU should be interlocked with core passage AHU, In case of power failure, core area AHUs should be tripped before the core passage AHUs to avoid cross contamination.. |  |
| - Power failure and restart requirement |  |
| The system will stop automatically upon loss of electricity and switches on manually after restoration of power. |  |

| - CONTAINMENT |  |
| --- | --- |
| - Explosion Protection |  |
| Not required |  |
| - Containment of the Product |  |
| Close/open system | Close |
| Leak proof | Required |
| Filtered air | Required |

| - SUPPORT REQUIRED FROM SUPPLIER |  |
| --- | --- |
| - Pre-installation support |  |
| Before manufacturing of AHUs, supplier shall send one copy of equipment drawing for approval. |  |
| - Start-up support |  |
| - Technical staff of supplier shall come to install the equipment and shall be present upto successful performance qualification run. - Technical staff of supplier shall train the applicable equipment operator of before operation Qualification testing. - Technical staff shall help to prepare the SOP of operation, cleaning and Preventive maintenance of the equipment. |  |
| - Documentation (write Yes or No as required) |  |
| ##### Document Name | ##### Yes/ No |
| ##### Test Certificates for Bought out items | ##### Yes |
| ##### Cable Termination details of all field instruments | ##### Yes |
| ##### Ducting Lay out | ##### Yes |
| ##### P&ID of Equipment | ##### Yes |
| ##### Technical specification | ##### Yes |
| ##### Basis of Design | ##### Yes |

- PERFORMANCE SPECIFICATION

HVAC System should be capable to achieve differential pressure, temperature, RH, cleanliness class and no. of Air changes per hour as per the enclosed Annexure 1.

| - VALIDATION REQUIREMENT WITH SCOPE (WRITE YES OR NO AS REQUIRED) |  |  |
| --- | --- | --- |
| Validation topic | Yes/ No | Scope |
| Design Qualification | ##### Yes | ##### User and Supplier |
| Installation Qualification | Yes | ##### User |
| Operational Qualification | Yes | ##### User |
| Performance Qualification | Yes | ##### User |
| ### Any Other | ##### No | ##### Not applicable |