# Design QUALIFICATION

# NAME OF THE ITEM: WOOD FIRED BOILER-CPD 60S

# FUNCTIONAL AREA:  BETA-LACTAM BLOCK

# PROTOCOL No. :        DQ/EU/007-00

Alkem LABORATORIES LIMITED BADDI (UNIT-II)

village & po: thana, near baddi,

dist.: solan, himachal pradesh

CONTENT

Sr. No.	  Description

- Protocol Approval

- Objective

- Responsibility

- Equipment Description & Identification

- User Requirements

- Complementary Aspects

- Safety and Environmental Protection

- Cleaning maintenance and service

- Rules and Regulation

- Scope of Delivery

- Installation ,Commissioning and Tests

- Qualification /Validation

- Guarantee/Warrantee

- Deviation

- Annexure

- Summary and Conclusion

- Approval of Design Qualification

- Acceptance by vendor

- PROTOCOL APPROVAL:

Protocol Prepared By:

| Functional area | Name | Signature | Date |
| --- | --- | --- | --- |
| Engineering |  |  |  |

DQ Reviewed By:

| Functional area | Name | Signature | Date |
| --- | --- | --- | --- |
| Engineering |  |  |  |
| Production |  |  |  |
| Quality Assurance |  |  |  |

DQ Approved By:

| Functional area | Name | Signature | Date |
| --- | --- | --- | --- |
| Head Engineering |  |  |  |
| Head Manufacturing |  |  |  |
| Head Quality |  |  |  |

- Objective:

The purpose of this document is to ensure that all the critical aspects of the Equipment,

cGMP & Safety features have been considered in designing the equipment/instrument and

is properly Documented

- Responsibilities:

In accordance with the document, following functions shall be responsible for initiation and finalization of Equipment user requirement specification. When the work is carried by contract/ consulting staff, all the work is to be performed under the oversight of Alkem.

3.1 Preparation of Document

- User department to prepare the DQ

- Ensures that the document is in compliance with current policies and procedures of cGMP regulations.

- Ensures that the content is sufficient, clearly defined, technically sound and accurate.

- It is a Guidance document to prepare the DQ.

# 3.2 Review of Document

- To be reviewed by Head of the user department and functional department ( Engineering & Quality assurance)

# 3.3 Approval of Document

- Approval of document by Head Manufacturing/Head Engineering/Head Quality.

# 4.0	Equipment Description & Identification:

# 4.1       Scope:      Wood fired Boiler

# 4.2      Purpose:   Purpose of wood fired boiler the fuel is burnt in the combustion chamber and heat realsed during combustion is transferred to water in membrane tubes and in shell. Adequate volume has been provided in the combustion chamber to allow complete combustion of fuel. The hot gases generated in furnace are enclosed in the membrane panel and are guided by the sides of the panel to first pass through the smoke tubes of the shell. in membrane panel, by means of radition and convection heat is transferred to water inside the tubes through tubes and fins of membrane panel and evaporation from water converted into steam.

  - Constructional features:

    - Shell & tube exchanger Pressure part

# Shell has tube plate on each end and the smoke tubes are welded to tube sheets. The shell is provided with water inlet, steam outlet, air vent, hand holes, manhole, lowdown and nozzles for connecting riser and down comer pipes.

    - Membrane panel assly:

# Membrane panel consists of water tubes emanating from two-bottom header, connected to top header. The top header is connected to riser header by means of top header connectors. The gap between the tubes is bridged by a metal strip, which also acts like a fin. The construction of membrane panel is a roof type, slopping at the top. The membrane panel as connected to shell by risers and down comers.

    - Furnace

# At the bottom,refractory bricks form four walls of the furnace. The refractory furnace is rectangular in cross section.The refractory work is done insde the furnace structure which is made of ISMC members to take the load MPA.Two bottom headers of the members provided in furnace structure.The membrane panel encloses two sides pf furnace and roof of furnace.other sides of furnace are enclosed by refractory.Membrane panel keeps the furnace water-cooled.

    - Heat recovery system (APH/WPH)

The air heater is  Shell and tube type heat exchanger. This is placed at the outlet of the bolier .The FD fan is connected to air side of this preheater.As the flue gases from the boiler pass through the tubes of the air heater,the FD air flowing over the tube banks of air preheater gets heated up thus providing pre-heated air for combustion.water pre-heater is non pressurized shell and tube heat exchanger in which flue gas passed through tubes.Here the heat is recovered by preheating the water going into system.

    - Dust collector

The Dust collecter is a simple cyclone seprator using centrifugal force for sepration of partial. It is placed after the HRU in flue gas path to seprate the dust particales.

  - USER REQUIREMENTS

  - System Requirements:

| Sr. No. | SYSTEM COMPONENTS | SYSTEM REQUIREMENTS |
| --- | --- | --- |
| 1 | Identification (In case of Equipment /Instrument) | Wood fired boiler |
| 2 | Model/Type | Wood fired boiler CPD-60S with horizontal Multi tabular shell type smoke tube with water wall furnace. |
| 3 | Capacity | 6000 Kg/hr |
| 4 | Potential Suppliers | - Thermax |
| 5 | Non metallic contact parts (In case of Equipment /Instrument) | 1. Durable. 2. Must be easily cleanable. |
| 6 | Motor & Electrical installations (In case of Equipment /Instrument) | Machine should be operated through on separate electrical control panel. |
| 7 | Packaging & Transport | Should be packed and transported in such a way to avoid any damage during transportation. |
| 8 | No. of requirements | 01 |
| 9 | Requirements for any power failure backup’s (In case of Equipment /Instrument) | To be backed up by installed in-house DG set. After any power failure PLC show continuous counting of all filled & sealed vials. |
| If any other please specify |  |  |
| 10 | Machine specification | - Centrifugal feed water pumps with motors and base frame. - Induced draft fan with coupled with motor base frame. - Primary forced draft with motor and base frame. - Secondary fan with motor. - Primary air inlet. - Firing/pocking doors. - Ash removing Doors. - Bigger fire doors for wood. - IBR piping Between feed water pumps and boiler. - Non return valve on feed water pump discharge line. - Stop valves on feed water pump discharge linr. - Main steam stop valves. - Single port spring loaded safety valves - Air vent valves. - Isolating valve for pressure gauge on feed water line. - Isolating valve for inspector pressure gauge. - Gauge glasses with shields. - Blow down valve for membrane. - Main shell blow down valve. - Isolating valve for water level controller. - Drain valve for level controller. - Magnetic water level controller. - Steam pressure switch for combustion control. - Pressure gauge for measuring steam pressure. - Pressure gauge for measuring water pressure. - Temperature indicator cum alarm for high flue gas temperature. |
| 11 | Safety features | Adequate safety features for men and material are provided along with the equipment. |
| 12 | Qualifications/ Documentations | The manufacturer shall complete and provide the documents pertaining to Design, Installation, and Operation Qualification. |
| 13 | Control System | - The electrical system of the equipment shall be housed as per cGEP standards, with adequate safety. - Electrical panel and electro pneumatic panel to be installed on the base structure inside the machine. - Control panel to be housed inside the machine. |
| 14 | Electrical panel | Should be consisting of two section - One for power ( Incorporating necessary, switchgears, fuses etc.) - One for control (Incorporating the necessary control logics.) |

Verified By & Date:

  - Technical Description

    - Specification of components.

| Sr. No. | Components | Descriptions |
| --- | --- | --- |
| 1 | Boiler Type | Horizontal multi-tabular shell type smoke tube with water wall furnace. |
| 2 | Max Steam output | 6000 Kg/hr |
| 3 | Outlet steam pressure | Should be 10.54 kg/cm2 |
| 4 | Outlet steam temperature | Should be 185oC |
| 5 | Dryness fraction | 0.97 |
| 6 | Safety valve set pressure | 10.54 -17.5 Kg/cm2 |
| 7 | Mode of firing | Manual |
| 8 | Type of grate | Horizontal fixed grate |
| 9 | Grate area | 8.16 m2 |
| 10 | Temperature profiles | At boiler outlet-280oC At HRU outlet-180oC |
| 11 | Design code | IBR 1950 with latest amendments |
| 12 | Design pressure | 10.54-17.5 kg/cm2 |
| 13 | Shell OD | 2150 mm |
| 14 | Shell length | 3000 mm |
| 15 | Tubes Shell OD X thickness | 76.2X3.66 mm |
| 16 | Total quantity | 222 nos |
| 17 | Tubes membrane panel ODX thickness | 63.5X3.6 mm |
| 18 | Steam safety valve (10.54) | Size-40X80 |
| 19 | Steam safety valve (17.5) | Size-25X50 |
| 20 | Shell blow down valve | Size-40 mm |
| 21 | Gate valve MPA blowdow | Size-25 mm |
| 22 | Stop valve in feed line | Size-25/40 mm |
| 23 | NRV in feed line | Size-25/40 mm |
| 24 | Feed water pump (10.54 kg/cm2) | Make- Gurndfos Type - Centrifugal multistage Capacity – 6.71 m3/hr Connected load-5.5 HP |
| 25 | Feed water pump (17.5 kg/cm2) | Type - Centrifugal multistage Capacity – 6.71 m3/hr Connected load-10 HP |
| 25 | Primary forced draft fan | Flow-180 m3/min Head @30 oC- 80 mmwc Connected load -7.5 HP |
| 26 | Induced draft fan for unit without MDC | Flow-265 m3/min Head@180 OC – 258 mmwc Connected load-30 HP |
| 27 | Induced draft fan for unit with MDC | Flow-360 m3/min Head@180 OC -258 mmwc Connected load- 40 HP |
| 28 | Air pre heater Model | 70 |
| 29 | Water Pre heater | 60 |
| 30 | Dust collector model (MDC) | MTSA 16 |
| 31 | Water level gauge glass | Qty-2 Size-400 mm |
| 32 | Level controller | Selectron DTC 503 |

Verified By & Date:

  - Utility Requirment:

| Sr no | Specification | Requirment |
| --- | --- | --- |
| 1 | Electrical supply | 3 Phase ,415 V AC ,50 HZ |
| 2 | Soft water | @ 7 -5 kg/cm2 |

Verified By & Date:

  - Material of Construction

  - 5.5.1 Contact and Non contact surfaces.

| # Sr. No |  | # Component Description | # MOC |
| --- | --- | --- | --- |
| 1 | Shell | SA 515/516 Gr.70 or equivalent |
| 2 | Tubes | ERW-BS 3059 |

# Verified By & Date:.

6.0      COMPLEMENTARY ASPECTS

6.1       Training

| Sr. No. | Specification |  | SYSTEM REQUIREMENTS |
| --- | --- | --- | --- |
| 1 | The vendor Shall supply all available information for the adequate exploitation of equipment. For the Compliance of this purpose at the Job site and/ or at the Vendors Shop. Vendor’s technical staff shall train customer’s personnel. The scope of the Training will be agreed during the contract signature. |  | YES |
| 2 | The supplier is to include the personnel training activities. The contractor is to specify the foreseen time for: - Operator/Supervisor training - Manager Training - Electrical maintenance training - Mechanical Maintenance training |  | YES |
| 3 | The contractor is to specify the personnel background needed for each of the operators maintenance. |  | YES |
| 6.2 Pre Delivery Qualifications (FAT) |  |  |  |
| Sr. No. |  | Specification | SYSTEM REQUIREMENTS |
| 1 |  | The System or its parts as provided for in the scope of supply shall be pre-installed at the vendors shop prior to delivery to customer site. Installation will be completed and documented including mechanical parts as well as electrical connections of all parts to facilitate taking over tests at Vendors shop prior to delivery. | YES |

6.3 Supplier Technical Documentation Requirements:

| Sr. No. | COMPONENTS | REQUIREMENTS |
| --- | --- | --- |
| 1. | Technical Documents | FAT,IQ,OQ Electrical Drawing P & ID diagram GA diagram Calibration certificates Bought out components certificates. |

Verified By & Date

6.4    Technical Manuals

| Sr. No. | Specification | Requirements |
| --- | --- | --- |
| 1. | Operation manual |  |

Verified By & Date

7.0 SAFETY AND ENVIRONMENTAL PROTECTION

| Sr No. | Specification |  | Requirements |
| --- | --- | --- | --- |
| 1 | Environment |  | NA |
| 7.1 Safety and Interlocking |  |  |  |
| 1 | Flue gas temperature control. | Electronic temperature switch. |  |
| 2 | Extra low water level in boiler. | Level controller alarm & boiler trip. |  |
| 3 | Very extra low level fusible plug | Fusible plug blow |  |
| 4 | Steam pressure high | Pressure switch alarm & boiler trip |  |
| 5 | Stack temp high | Temperature switch alarm & boiler trip |  |

Verified By & Date:

8.0 CLEANING MAINTENANCE AND SERVICE

| Sr No. | Specification |
| --- | --- |
| 1. | In accordance with cGMP guidelines the units must be easy to clean, to disinfect, and where necessary, to sterilize. |
| 2. | The Supplier should guarantee that, if required, a service team can be on site within one working day. |
| 3 | The design should be such as to allow mechanical cleaning of the surface and that the cleanliness of the surface can be checked easily. |
| 4 | All machine parts, in particular instrumentation, should be constructed so that they can be easily removed and calibrated. |
| 5 | All special tools required for running and maintenance should be best. |
| 6 | A spare parts delivery guarantee with in time. |

Verified By & Date:

9.0 RULES AND REGULATION :

These standards, recommendation and requirements are considered  the minimum. Specifications that are more stringent or expansive take the precedence. In case of conflict between published requirements, final determination is the responsibility of the Owners Representative.

10. SCOPE OF DELIVERY

| Sr No. | Specification | Requirements |
| --- | --- | --- |
| 1 | Units described in the specific system requirements including all necessary controls and instrumentation. | YES |
| 2 | The complete mechanical and electrical installation. | YES |
| 3 | The Connections to all the necessary utilities, exhaust, and waste lines necessary for its operation. | YES |
| 4 | All piping and cabling of the units itself. | YES |
| 5 | Wiring and cable run: all wiring and cable run is part of the supply. Alkem laboratories Ltd will supply the main power switches to be located in correspondence to the electrical and control cabinets delivered by the equipment supplier. | YES |
| 6 | All internal contacts of the supplied equipment for the required utilities. | YES |
| 7 | Unload on site of the equipment: the supplier is required to define all the necessary handling devices required to the unloading operation. The supplier will inform at least 4 weeks in advance the day of delivery and the list of required handling devices. | YES |
| 8 | Assembling operation: the required consumable, the internal transportation, the assembling tools and the required personal are part of the supply. | YES |
| 9 | A complete set of commissioning spare parts. | YES |
| 10 | All special tools necessary for use and maintenance of the supplied equipment. | YES |
| 11 | A complete set of two years spare parts should be listed quoted and offered as option. | YES |
| 12 | All test activities as specified in this document. | YES |
| 13 | Training in the use and maintenance of the equipment. | YES |
| 14 | A complete set of documentation as specified In this document. | YES |

Verified By & Date:

11.0	 INSTALLATION, COMMISSIONING AND TESTS

11.1    General

| Sr.No. | Specification | Requirements |
| --- | --- | --- |
| 1. | The Contractor must specify for each piece of equipment the Guaranteed performance and the guaranteed system performance. These values will be tested during the acceptance tests. | YES |
| 2 | In addition the functionality described in the user requirements and detailed in the system specifications will be tested. | YES |

11.2 INSTALLATION, COMMISSION

| Sr. No. | Specification | Requirements |
| --- | --- | --- |
| 1 | The commissioning tests will be carried out in accordance with a written test plan developed by the supplier with clearly stated test procedures and acceptance criteria. | YES |
| 2 | The contractor will approve successfully completed tests and will specify items requiring additional work. Representatives from Alkem Laboratories Ltd. Will attend and participate in the commissioning tests as required. | YES |
| 3 | The installation and commissioning of the system will be performed at the Alkem Laboratories Ltd. Facility by the contractor. | YES |
| 4 | The commissioning can only start once all the foreseen documents have been delivered by the supplier to Alkem Laboratories Ltd. | YES |
| 5 | All equipment should be properly installed, adjusted, leveled, tagged, and connected with utilities. | YES |
| 6 | Point to point checks on wiring and pneumatic should be performed. | YES |
| 7 | All instruments should be properly calibrated. | YES |
| 8 | A equipment ( instrument) used for qualification must be listed and approved by Alkem Laboratories Ltd. | YES |
| 9 | The calibration equipment must have all the necessary documents to demonstrate their maintenance & use. | YES |
| 10 | The last calibration of all this equipment must be less than 6 months old, and evidenced by certificate. | YES |
| 11 | Verification that the interior surfaces of equipment are free of practices and dirt and all points of product contact meet the specified material requirements. | YES |
| 12 | All the clearances and tolerances specified in the drawing or recommended by component manufacturers are correct. | YES |
| 13 | On site verification that valves and other equipment with moving parts are in their normal position if in a power down condition and move in the correct direction with the correct speed and precision. | YES |
| 14 | Verification that all the Input and Output points are connected and labeled according to the documentation and that all the along the input values have been scaled in accordance with the system specification and process requirements. That all equipment components requiring configuration | YES |
| 15 | The commissioning should demonstrate that the system supplied by the contractor has been properly installed and that the functions are in accordance with Alkem Laboratories Ltd. User Requirements specifications, Vendors System specifications Manuals and other Documentation. | YES |

11.3 Site Acceptance Test   (SAT)

| Sr. No. | Specification | Requirements |
| --- | --- | --- |
| 1. | This test will be carried out once the commissioning will be completed. The scope will be to verify the performance and the functionality of the system integrated with the other factory systems | YES |
| 2 | The test will be carried out to verify the system response with the expected productivity of the system. | YES |
| 3 | Details on the test realization will be defined during the project Phase. The supplier is asked to specify the proposed duration for SAT and the standard procedure proposed. | YES |
| 4 | During SAT the required functionality, performances and system reliability are met. | YES |
| 5 | The Functionality described in the User Requirements Specification and in the System Specifications are verified and met. | YES |
| 6 | All the documentation agreed has been delivered. | YES |

Verified By & Date:

12.0 QUALIFICATION / VALIDATION

| Sr.No. | Specification | Requirements |
| --- | --- | --- |
| 1. | The maintenance Qualification is responsibility of the customer. However, the supplier is responsible for delivering the basic documents for maintenance qualification. | YES |
| 2. | This includes all side costs such as: calibration measuring equipment and instruments: manpower (IQ and OQ will take place completely on Alkem Laboratories Ltd.) | YES |
| 3 | Time Schedule for IQ/OQ execution will be developed by Alkem Laboratories Ltd. With the supplier. | YES |
| 4 | Suppliers personnel used for IQ/OQ must be well trained and experienced. This should be documented. | YES |
| 5 | The onsite test run performed by the supplier might become part of the IQ. | YES |
| 6 | Main IQ/OQ steps such as calibration must be performed and documented in accordance to a SOP approved by Alkem Laboratories Ltd. | YES |
| 7 | All equipment used for qualification must be listed and approved by Alkem Laboratories Ltd. The calibration equipment should be well documented. | YES |
| 8 | The last Recalibration of all this equipment should be less than 06 month old. Proofed by Certificate. | YES |
| 9 | OQ can only start after IQ approved by Alkem Laboratories Ltd. | YES |
| 10 | IQ will be carried out by Alkem Laboratories Ltd. During Installation phase. IQ will include the tests performed by the contractor. | YES |
| 11 | Part of the OQ will be carried out by Alkem Laboratories Ltd. During commissioning and SAT phase. OQ will include the tests performed by the contractor. | YES |
| 12 | After installation of the equipment at customers site. Complementary IQ & OQ tests will be performed by the Customer and may be supervised by a member of Technical staff. | YES |
| 13 | Qualification documents (In case of equipments/Instruments) | DQ, IQ, OQ |

Verified By & Date:

13.0 GAURANTEE/WARRANTEE

| Sr.No. | Specification | Requirements |
| --- | --- | --- |
| 1. | The System must be guaranteed including all the sub- system and components for a period of 12 months from the date of the system acceptance for a 03- shift operation. | YES |
| 2 | The servicing companies involved for the Sub- systems maintenance must be declared and the maintenance group organization described. Furthermore, the contractor will be directly responsible of the system assistance and the required operation will be co- ordinate by him. | YES |
| 3 | In case of failures, the intervention will be guaranteed by the contractor within a maximum time limit. The contractor is asked to specify the maximum time limit. | YES |
| 4 | The supplier is asked to propose as option maintenance and assistance contract after the guarantee expiration. | YES |

Verified By & Date:

# 14.0 Deviation

# 15.0 Annexure

# 16.0 Summary and Conclusion

# 17.0 Approval of Design Qualification.

| Functional area | Name | Signature | Date |
| --- | --- | --- | --- |
| Head Engineering |  |  |  |
| Head Manufacturing |  |  |  |
| Head Quality |  |  |  |

# 18.    Acceptance By vendor

# Name of Vendor:

# Sign/Date: