# Design QUALIFICATION

# NAME OF THE ITEM: AIR HANDLING UNIT - 1

# FUNCTIONAL AREA:  PRODUCTION BLOCK

# PROTOCOL No. :        DQ/

ALKEM HEALTH SCIENCE

SAMARDUNG, KAREK BLOCK,

PO. NAMTHANG,

SOUTH SIKKIM-737137

CONTENT

Sr. No.	  Description

- Protocol Approval

- Objective

- Responsibility

- Equipment Description & Identification

- User Requierments

- Complementary Aspects

- Safety and Environmental Protection

- Cleaning maintenance and service

- Rules and Regulation

- Scope of Delivery

- Installation ,Commissioning and Tests

- Qualification /Validation

- Guarantee/Warrantee

- Deviation

- Annexure

- Summary and Conclusion

- Approval of Design Qualification

- Acceptance by vendor

- PROTOCOL APPROVAL:

Protocol Prepared By:

| Functional area | Name | Signature | Date |
| --- | --- | --- | --- |
| Engineering |  |  |  |

DQ Reviewed By:

| Functional area | Name | Signature | Date |
| --- | --- | --- | --- |
| Engineering |  |  |  |
| Production |  |  |  |
| Quality Assurance |  |  |  |

DQ Approved By:

| Functional area | Name | Signature | Date |
| --- | --- | --- | --- |
| Head Engineering |  |  |  |
| Head Manufacturing |  |  |  |
| Head Quality |  |  |  |

- Objective:

The purpose of this document is to ensure that all the critical aspects of the Equipment, cGMP & Safety features have been considered in designing the equipment/instrument and is properly documented

- Responsibilities:

In accordance with the document, following functions shall be responsible for initiation and finalization of Equipment user requirement specification. When the work is carried by contract/ consulting staff, all the work is to be performed under the oversight of Alkem

3.1 Preparation of Document

- User department to prepare the DQ

- Ensures that the document is in compliance with current policies and procedures of cGMP regulations.

- Ensures that the content is sufficient, clearly defined, technically sound and accurate.

- It is a Guidance document to prepare the DQ.

# 3.2 Review of Document

- To be reviewed by Head of the user department and functional department ( Engineering & Quality assurance)

# 3.3 Approval of Document

- Approval of document by Head Manufacturing/Head Engineering/Head Quality.

# 4.0	Equipment Description & Identification:

# 4.1       Scope:        Multiple Effect Distillation unit

# 4.2        Purpose:   To produce Water for injection

  - USER REQUIREMENTS

  - System Requirements:

| Sr. No. | SYSTEM COMPONENTS | SYSTEM REQUIREMENTS |
| --- | --- | --- |
| 1 | # Equipment | # Details of Make, Name, Serial. No., Capacity, Model and Year of manufacture should be available |
| 2. | # Specification | # Including all Standard accessories with following Scope of Supply: - Basic Machine Multiple Effect Distillation Unit with PLC system in SS 316 Contact parts. - Recommended spare. - PLC & HMI - Outer column Shell - Condensor - Feed water and cooling water cooler. - Contact parts- SS 316L - Non contacts parts-SS 304 |
| 3. | # Capacity | # 500 LPH at 3 Kg/Cm2 Boiler Steam |
| 4. | # Model | - The equipment should be a cGMP model, in terms of surface finish, absence of sharp corners, clean ability, assembling and dismantling of components and control system for its intended use. |
| 5. | # Process | - Equipment should be able to produce pure steam. |
| 6. | # Material of Construction | - Outer column shell,Condensor,Sampling Preheater should be made up of SS 316L & all other non-contact components are of SS 304 - Exterior easy to clean, disinfect and non-corrosive. - Material test certificates to be provided. |
| 7. | # Calibration | - All components that require calibration shall be identified and calibrated. - Calibration certificates to be provided at the time of Installation Qualification. - Test certificates/calibration charts of sensors & control instruments to be provided. |
| 8. | # Safety Features | - Adequate safety features for men and process shall be provided along with the equipment. - Feed water pump pressure sensing shall be provided. |
| 9. | # Control System | - The Equipment shall be controlled through PLC based system. |
| 10. | # Qualification / Documentation | - The manufacturer shall complete and provide the documents pertaining to Design, Installation & Operation Qualification and detail functional specifications including control system with screen design of operating terminal. - Alarms & Interlocks. - Information on purchased/bought-out parts. - Circuits & interlocks details. - Operating Manual - Trouble shooting tips. - Preventive maintenance schedules. - Safety Precautions. |
| 11. | Conductivity | Should be Less than 1.3µs/cm at 25o C |
| 12. | TOC | Should be Less than 500 ppb |
| 13. | Endotoxin | Should be Less than 0.250 EU / ml |
| 14. | Bacteria (TVC) | Should be Less than 10 cfu/100 ml |
| 15. | Heavy Metal | Should be NMT 0.1 PPM |
| 16. | Nitrates | Should be NMT 0.2 PPM |
| 17. | PH | Should be 5 – 7 at 25ºC |
| 18. | Operation | Automatic with real time printing |
| 19. | Construction Feature | As per GMP Contact surfaces-Round corner Nozzles-Triclover,Fitting-Sanitary |
| 20. | Available room size for Equipment |  |

Verified By & date:

  - Technical Description

| Sr. No. | Specification | SYSTEM REQUIREMENTS |
| --- | --- | --- |
| 1 | Capacity | 500 LPH at 3 Kg/Cm2 Boiler Steam |
| 2 | Operation | Automatic with PLC and HMI |
| 3 | Outer Column shell | Operating Temp.165 OC Operating pressure 6 Kg / Cm² Design Pressure – 7 Kg / Cm² Design Temperature – 175º C Hydrostatic Test Pressure – 9 Kg / Cm² Inside surface finish – < 0.6 Ra, Electro Polished Outer surface finish – Mirror (Mechanical Polished |
| 4 | Condenser (Inner column) | Operating Temp.165 OC Operating pressure 6 Kg / Cm² MOC 316L Design pressure – 7 Kg / Cm² Design Temperature – 175º C Hydrostatic Test Pressure – 9 Kg / Cm² Inside surface finish- Mili polished Outer surface finish < 0.6 Ra Electro Polished Tube side Operating Pressure – 6 Kg / Cm² Operating Temperature – 165º C MOC -316L Design pressure – 7 Kg / Cm² Design Temperature – 175º C Inner and outer finish—Mili polished Outer surface finish (Contact Parts) – < 0.6 Ra Electro Polished |
| 5 | Feed water and cooling water cooler | Shell side Operating Pressure – 1 Kg / Cm² Operating Temperature – 100º C Design pressure – 7 Kg / Cm² Design Temperature – 175º C Hydrostatic Test Pressure – 9 Kg / Cm² MOC - SS 316L Inside surface finish – < 0.6 Ra, Electro Polished Outer surface finish – Mirror (Mechanical Polished) Tube side Operating Pressure – 6 Kg / Cm² Operating Temperature – 100º C Design pressure – 7 Kg / Cm² Design Temperature – 175º C MOC - SS 316L seamless tube Outside surface finish – Electro Polished Internal surface finish – Mill Polished |
| 6 | Stand | MOC – SS 304 Square / Rectangle pipe Mounting – Leg mounting (Adjustable 50 mm ) Surface finish – Mirror (Mechanical Polished) |
| 7 | Insulation Cladding | Riveted Cladding MOC – SS 304 Outer surface finish – Mirror polished (Mechanical Polished) Insulation thickness – 50 mm (Uncompressed) Insulation material – Resin Bonded Glass wool with “K” Factor 0.39 W / mk |
| 8 | Gasket | PTFE / Silicon Type - Food Grade Temperature – 200º C |
| 9 | Overall Dimension of machine | 134” L x 111” W x 58” H |

Verified By & date:

  - Detail of components:

| Sr. No | Components | Specification |  |
| --- | --- | --- | --- |
| 1. | Feed Pump | Make Make Rated Head Rated flow rate MOC Mechanical seal Motor Location | CRN 3 -12 Grundfos 57.1 meter 3000 LPH SS316 SiC/SiC 3 Phase, 380/415 V, 2853 RPM, 1.10 KW At the inlet of the feed water |
| 2. | Cooling Pump | Make Model Rated Head Rated flow rate MOC Mechanical seal | Grundfos CM3-2 13.3 meter 3100 LPH SS316 SiC/SiC Location At the inlet of the cooling water |
| 3. | Non return valve | Make Model MOC Size | Make Alfa Laval (LKM) Model LKC - 2 MOC SS 316L DN 25 (Triclover End Connection) Location 1 At the cooler air vent line Location 2 At the WFI Rejection Line |
| 4. | Variable flow meter | Make Model MOC Range | George Fishcer 335 Tube -Polyamide Float -PVDF Gaskets -EPDM 100 – 1000 LPH Location 1 At discharge side of feed pump Location 2 At discharge side of cooling pump |
| 5. | Sampling VAlve | Make MOC Diaphragm | Make Pharmalab MOC SS 316L Silicon |
| 6. | WFI sampling Valve | Make MOC Size Diaphragm | Pharmalab SS 316L DN-38 (Butt End connection) Silicon |
| 7. | Pneumatic valve | Make Model MOC of working parts MOC of Body Type Size Seal Actuator | Make Gemu Model 554 SS 316L SS 316L Pneumatically Operated Angle Seat DN 15 / 20 (Butt End connection) P.T.F.E Single Acting (Spring Return) Location 1 At Last Column Purging Line Location 2 At Cooler Water Inlet Line |
| 8. | 2 way Pneumatic Valve | Make MOC of Working Parts MOC of Body Type Size Seal Actuator | Gemu SS 316L SS 316L Diaphragm DN 15 / DN 20 (Butt End connection) P.T.F.E Single Acting (Spring Return) Location 1 At cooler air vent line Location 2 At feed water inlet line |
| 9. | Globe Valve | Make Model MOC of Working Parts MOC of Body Type Size Seal Location 1 | Shakti Non IBR SS 410 Gun Metal Globe valve 40 MM Teflon Location Plant Steam Inlet |
| 10. | Diaphragm Valve | Make MOC Diaphragm Size | Crane Process SS 316L PTFE / EPM DN-25 (Triclover End Connection |
| 11. | Air regulator (Filter, Regulator, Lubricator | Make Range Location | Festo 0 – 16 Kg / Cm² At the Inlet of the compressed air |
| 12. | Steam Trap | Make Model Type Max working Pressure Max.temperature Location 1 | Spirax BPT-21,15 NB (Threaded End Connection) Balanced pressure thermostatic trap 21 Kg / Cm² 285° C At First column air vent line Drain |
| 13. | Safety Valve | Make Spirax Model SV11 MOC G.M Size Range Location | Spirax SV11 G.M 25 mm (Threaded end connection) 75-125 PSI At inlet of the plant steam line |
| 14. | Pressure gauge | Make MOC Dial size Type Range Location | Waaree SS 316 (Contact ) (Threaded End Connection) 100 mm Bourdon tube 0-16 Kg/cm² At plant steam line |
| 15. | Pressure gauge | Make MOC Dial size Type Range Mounting Dampening liquid Location | Waaree SS 316L (Contact parts) 100 mm Diaphragm 0-16 Kg/cm² Sanitary (Triclover End Connection) Glycerin At discharge side of feed pump |
| 16. | Control panel | Model Enclousure Panel Location Size Contractor, OR 1,3 pole rotary switch PLC HMI Transformer Emergency Push button | Automatic with manual operation Rittal On the Skid 800X1000X300 L & T Salzer Allen Bradley PVP 400 Spike/Bhatt Magnatic/Narmda Schneider |
| 17. | Conductivity meter | Model Make Display Input Channel Output Alarm Location | DG402G Yokogawa LCD two line From Conductity sensor Dual channel 4-20 ma Relay type On control panel |
| 18. | Conductivity sensor | Make End connection MOC Temp Range Location 1 Location 2 | Yokogawa Triclover and connection SS316 0 oC- 110 oC,1350 C for 30 min At inlet of feed pump At the WFI outlet line |
| 19. | Temperature sensor | Make MOC Range Type Connection Location 1 Location 2 Location 3 | Radix SS316L -50 0C to 200o C PT 100/A Triclover At the Boiler steam inlet line At the WFI water outlet line At the cooling water outlet line |
| 20. | Sanitary pressure Switch | Make MOC Diapharm Range Location | Orion SS 316L Teflon 0.2-2.6 bar At inlet side of feed pump. |
| 21. | Sanitary pressure Switch | Make MOC Diapharm Range Location | Orion SS316 Teflon 1-15 BAR At the discharge side of feed pump |
| 22. | pressure Switch | Make MOC Diapharm Range Location | Orion SS 316L Teflon 0.2-2.6 bar At inlet side of Cooling pump. |
| 23. | pressure Switch | Make MOC Diapharm Range Location | Orion Aluminium Teflon 0.2-7 Bar At Comp.air inlet |
| 24. | Liquid level sensor | Make MOC Size Type Location 1 Location 2 | E+H/Burket SS316L !” TC Fork type First column Second column |
| 25. | Disposal Vent filter | Make Model Filter Length Medium Removal Rate Location | Pall KA1PFRP1 4.6” M PTFE 0.2 Micron At Cooler Air Vent Line |
| 26. | Printer | Make Model Location | EPSON LX-300 + II, 80 column, Dot Matrix Beside panel board |

Verified By & date:

5.4      Utility Details:

| Sr no | Utility | Supply | Requirements |
| --- | --- | --- | --- |
| 1. | Boiler steam | At Min 3 kg/cm2 pressure and 143 C temperature | Min : 135 Kg/Hr |
| 2. | Feed Water | At Max. 2 Kg/cm2 Pressure & Ambient | 575 LPH |
|  | Cooling water | At 2 kg/cm2 Pressure & Ambient Temperature | 650 LPH |
| 3. | Electricity | At 415 V, 50 Hz, 3 Phase + Neutral + Earthing | 3 KW |
| 4. | Compressed Air | At 6 Kg/cm2 Pressure | 5 CFM |

Verified By & date:

6.0      COMPLEMENTARY ASPECTS

6.1       Training

| Sr. No. | Specification |  | SYSTEM REQUIREMENTS |
| --- | --- | --- | --- |
| 1 | The vendor Shall supply all available information for the adequate exploitation of equipment. For the Compliance of this purpose at the Job site and/ or at the Vendors Shop. Vendor’s technical staff shall train customer’s personnel. The scope of the Training will be agreed during the contract signature. |  | Yes |
| 2 | The supplier is to include the personnel training activities. The contractor is to specify the foreseen time for: - Operator/Supervisor training - Manager Training - Electrical maintenance training - Mechanical Maintenance training |  | Yes |
| 6.2 Pre Delivery Qualifications (FAT) |  |  |  |
| Sr. No. |  | Specification | SYSTEM REQUIREMENTS |
| 1 |  | The System or its parts as provided for in the scope of supply shall be pre-installed at the vendors shop prior to delivery to customer site. Installation will be completed and documented including mechanical parts as well as electrical connections of all parts to facilitate taking over tests at Vendors shop prior to delivery. | YES |

6.3 Supplier Technical Documentation Requirements:

| Sr. No. | COMPONENTS | REQUIREMENTS |
| --- | --- | --- |
| 1. | Technical Documents | FAT,IQ,OQ Electrical Drawing P & ID diagram GA diagram Calibration certificates of instruments Hydro test certificates Bought out components detail and certificates MOC certificates |

6.4    Technical Manuals

| Sr. No. | Specification | Requirements |
| --- | --- | --- |
| 1. | Operation manual |  |

Verified By & date:

7.0 SAFETY AND ENVIRONMENTAL PROTECTION

| Sr No. | Specification | Requirements |
| --- | --- | --- |
| 1. | Environment | NA |
| 7.1 Safety Alarms. |  |  |
| 1 | Operating air pressure low |  |
| 2 | Boiler steam temperature low |  |
| 3 | Distill water level high |  |
| 4 | Feed water suction pressure low |  |
| 5 | Feed water conductivity high |  |
| 6 | Feed water discharge pressure low |  |
| 7 | Insufficient evaporation |  |
| 8 | Purging on problem |  |
| 9 | Purging off problem |  |
| 10 | WFI conductivity high |  |
| 11 | WFI temperature high |  |
| 12 | WFI temperature low |  |
| 13 | Cooling water temperature high |  |
| 14 | Feed pump motor overload relay |  |
| 15 | Cooling pump motor overload relay |  |
| 16 | Insufficient cooling water |  |
| 7.2 | Interlocking for Feed pump and Control valve- Feed pump in WFI stops and Feed water valve Turn OFF automatically in following conditions |  |
| 1. 2. 3. 4. 5. 6. 7. 8. 9. 10. | Boiler steam temperature low Insufficient feed water Feed water conductivity high Insufficient evaporation Purging on problem Purging off problem Air pressure low Distill water level high Feed pump motor overload relay Emergency Stop |  |
| 7.3. | INTER LOCKING FOR COOLING PUMP AND CONTROL VALVE Cooling pump stops and cooling water valve turns OFF automatically when the following conditions arise. |  |
| 1. 2. 3. 4. 5. | Air pressure low WFI temperature low Cooling pump motor overload relay Insufficient cooling water Emergency stop |  |
| 7.4 | INTER LOCKING FOR PNEUMATIC VALVE DUMPING VALVE Dumping Valve turns ON automatically when the following conditions arise. |  |
| 1. 2. 3. 4. 5. 6. | Initial drain time Boiler steam temperature low WFI temperature low WFI conductivity high Air pressure low Emergency stop |  |
| 7.5 | AIR VENT VALVE: Air vent valve turns ON automatically when the Following conditions arise. |  |
| 1. | WFI temperature low |  |
| 7.6 | FIRST COLUMN DRAIN VALVE : Cooling water valve turns OFF when the following conditions arise. |  |
| 1. 2. | WFI temperature low Insufficient cooling water |  |

Verified By & date:

8.0 CLEANING MAINTENANCE AND SERVICE

| Sr No. | Specification | Requirements |
| --- | --- | --- |
| 1. | In accordance with cGMP guidelines the units must be easy to clean, to disinfect, and where necessary, to sterilize. | YES |
| 2. | The Supplier should guarantee that, if required, a service team can be on site within one working day. | YES |
| 3 | The design should be such as to allow mechanical cleaning of the surface and that the cleanliness of the surface can be checked easily. | YES |
| 4 | All machine parts, in particular instrumentation, should be constructed so that they can be easily removed and calibrated. | YES |
| 5 | All special tools required for running and maintenance should be best. | YES |
| 6 | A spare parts delivery guarantee with in time. | YES |

Verified By & date:

9.0 RULES AND REGULATION :

These standards, recommendation and requirements are considered  the minimum. Specifications that are more stringent or expansive take the precedence. In case of conflict between published requirements, final determination is the responsibility of the Owners Representative.

Verified By & date:

10. SCOPE OF DELIVERY

| Sr No. | Specification | Requirements |
| --- | --- | --- |
| 1. | Units described in the specific system requirements including all necessary controls and instrumentation. | YES |
| 2 | The complete mechanical and electrical installation. | YES |
| 3 | The Connections to all the necessary utilities, exhaust, and waste lines necessary for its operation. | YES |
| 4 | All piping and cabling of the units itself. | YES |
| 5 | Wiring and cable run: all wiring and cable run is part of the supply. Alkem Health Science will supply the main power switches to be located in correspondence to the electrical and control cabinets delivered by the equipment supplier. | YES |
| 6 | All internal contacts of the supplied equipment for the required utilities. | YES |
| 7 | Unload on site of the equipment: the supplier is required to define all the necessary handling devices required to the unloading operation. The supplier will inform at least 4 weeks in advance the day of delivery and the list of required handling devices | YES |
| 8 | Assembling operation: the required consumable, the internal transportation, the assembling tools and the required personal are part of the supply. | YES |
| 9 | A complete set of commissioning spare parts. | YES |
| 10 | All special tools necessary for use and maintenance of the supplied equipment. | YES |
| 11 | A complete set of two years spare parts should be listed quoted and offered as option. | YES |
| 12 | All test activities as specified in this document. | YES |
| 13 | Training in the use and maintenance of the equipment. | YES |
| 14 | A complete set of documentation as specified In this document. | YES |

Verified By & date:

11.0	 INSTALLATION, COMMISSIONING AND TESTS

11.1    General

| Sr.No. | Specification | Requirements |
| --- | --- | --- |
| 1. | The Contractor must specify for each piece of equipment the Guaranteed performance and the guaranteed system performance. These values will be tested during the acceptance tests. | YES |
| 2. | In addition the functionality described in the user requirements and detailed in the system specifications will be tested. | YES |

11.2 INSTALLATION, COMMISSION

| Sr.No. | Specification | Requirements |
| --- | --- | --- |
| 1 | The commissioning tests will be carried out in accordance with a written test plan developed by the supplier with clearly stated test procedures and acceptance criteria. | YES |
| 2 | The contractor will approve successfully completed tests and will specify items requiring additional work. Representatives from Alkem Health Science Will attend and participate in the commissioning tests as required. | YES |
| 3 | The installation and commissioning of the system will be performed at the Alkem Health Science | YES |
| 4 | The commissioning can only start once all the foreseen documents have been delivered by the supplier to Alkem Health Science | YES |
| 5 | All equipment should be properly installed, adjusted, leveled, tagged, and connected with utilities. | YES |
| 6 | Point to point checks on wiring and pneumatic should be performed. | YES |
| 7 | All instruments should be properly calibrated. | YES |
| 8 | A equipment ( instrument) used for qualification must be listed and approved by Alkem Health Science | YES |
| 9 | The calibration equipment must have all the necessary documents to demonstrate their maintenance & use. | YES |
| 10 | The last calibration of all this equipment must be less than 6 months old, and evidenced by certificate. | YES |
| 11 | Verification that the interior surfaces of equipment are free of practices and dirt and all points of product contact meet the specified material requirements. | YES |
| 12 | All the clearances and tolerances specified in the drawing or recommended by component manufacturers are correct. | YES |
| 13 | On site verification that valves and other equipment with moving parts are in their normal position if in a power down condition and move in the correct direction with the correct speed and precision. | YES |
| 14 | Verification that all the Input and Output points are connected and labeled according to the documentation and that all the along the input values have been scaled in accordance with the system specification and process requirements. That all equipment components requiring configuration | YES |

11.3 Site Acceptance Test   (SAT)

| Sr. No. | Specification | Requirements |
| --- | --- | --- |
| 1. | This test will be carried out once the commissioning will be completed. The scope will be to verify the performance and the functionality of the system integrated with the other factory systems ( Including sterility testing of at least 02 days). | YES |
| 2 | The test will be carried out to verify the system response with the expected productivity of the system. | YES |
| 3 | Details on the test realization will be defined during the project Phase. The supplier is asked to specify the proposed duration for SAT and the standard procedure proposed. | YES |
| 4 | During SAT the required functionality, performances and system reliability are met. | YES |
| 5 | The Functionality described in the User Requirements Specification and in the System Specifications are verified and met. | YES |
| 6 | All the documentation agreed has been delivered. | YES |
| 7 | The Functionality described in the User Requirements Specification and in the System Specifications are verified and met. | YES |
| 8 | All the documentation agreed has been delivered. | YES |

Verified By & date:

12.0 QUALIFICATION / VALIDATION

| Sr.No. | Specification | Requirements |
| --- | --- | --- |
| 1. | The maintenance Qualification is responsibility of the customer. However, the supplier is responsible for delivering the basic documents for maintenance qualification. | YES |
| 2. | This includes all side costs such as : calibration measuring equipment and instruments: manpower (IQ and OQ will take place completely on Alkem Health Science) | YES |
| 3 | Time Schedule for IQ/OQ execution will be developed by Alkem Health Science With the supplier. | YES |
| 4 | Suppliers personnel used for IQ/OQ must be well trained and experienced. This should be documented. | YES |
| 5 | The onsite test run performed by the supplier might become part of the IQ. | YES |
| 6 | Main IQ/OQ steps such as calibration must be performed and documented in accordance to a SOP approved by Alkem Health Science | YES |
| 7 | All equipment used for qualification must be listed and approved by Alkem Health Science The calibration equipment should be well documented. | YES |
| 8 | The last Recalibration of all this equipment should be less than 06 month old. Proofed by Certificate. | YES |
| 9 | OQ can only start after IQ approved by Alkem Health Science | YES |
| 10 | IQ will be carried out by Alkem Health Science During Installation phase. IQ will include the tests performed by the contractor. | YES |
| 11 | Part of the OQ will be carried out by Alkem Health Science During commissioning and SAT phase. OQ will include the tests performed by the contractor. | YES |
| 12 | After installation of the equipment at customers site. Complementary IQ & OQ tests will be performed by the Customer and may be supervised by a member of Technical staff. | YES |
| 13 | Qualification documents (In case of equipments/Instruments) | DQ, IQ, OQ |

Verified By & date:

13.0 GAURANTEE/WARRANTEE

| Sr.No. | Specification | Requirements |
| --- | --- | --- |
| 1. | The System must be warranty including all the sub- system and components for a period of 12 months from the date of the system acceptance for a 03- shift operation. | YES |
| 2 | The servicing companies involved for the Sub- systems maintenance must be declared and the maintenance group organization described. Furthermore, the contractor will be directly responsible of the system assistance and the required operation will be co- ordinate by him. | YES |
| 3 | In case of failures, the intervention will be guaranteed by the contractor within a maximum time limit. The contractor is asked to specify the maximum time limit. | YES |
| 4 | The supplier is asked to propose as option maintenance and assistance contract after the waranty expiration. | YES |

Verified By & date:

# 14.0 Deviation

# ------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------

# 15.0 Annexure

# ------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------

# 16.0 Summary and Conclusion

# ---------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------

# 17.0 Approval of Design Qualification.

| Functional area | Name | Signature | Date |
| --- | --- | --- | --- |
| Head Engineering |  |  |  |
| Head Manufacturing |  |  |  |
| Head Quality |  |  |  |

# 18.    Acceptance By vendor

# Name of Vendor:

# Sign/Date: