# Design QUALIFICATION

# NAME OF THE ITEM: NITROGEN PLANT

# FUNCTIONAL AREA:  PRODUCTION BLOCK

# PROTOCOL No. :        DQ/

ALKEM HEALTH SCIENCE

SAMARDUNG, KAREK BLOCK,

PO. NAMTHANG,

SOUTH SIKKIM-737137

CONTENT

Sr. No.	  Description

- Protocol Approval

- Objective

- Responsibility

- Equipment Description & Identification

- User Requirements

- Complementary Aspects

- Safety and Environmental Protection

- Cleaning maintenance and service

- Rules and Regulation

- Scope of Delivery

- Installation ,Commissioning and Tests

- Qualification /Validation

- Guarantee/Warrantee

- Deviation

- Annexure

- Summary and Conclusion

- Approval of Design Qualification

- Acceptance by vendor

- PROTOCOL APPROVAL:

Protocol Prepared By:

| Functional area | Name | Signature | Date |
| --- | --- | --- | --- |
| Engineering |  |  |  |

DQ Reviewed By:

| Functional area | Name | Signature | Date |
| --- | --- | --- | --- |
| Engineering |  |  |  |
| Production |  |  |  |
| Quality Assurance |  |  |  |

DQ Approved By:

| Functional area | Name | Signature | Date |
| --- | --- | --- | --- |
| Head Engineering |  |  |  |
| Head Manufacturing |  |  |  |
| Head Quality |  |  |  |

2.0	Objective:

The purpose of this document is to ensure that all the critical aspects of the Equipment,

cGMP & Safety features have been considered in designing the equipment/instrument and

is properly documented

3.0   Responsibilities:

In accordance with the document, following functions shall be responsible for initiation and finalization of Equipment user requirement specification. When the work is carried by contract/ consulting staff, all the work is to be performed under the oversight of Alkem.

3.1 Preparation of Document

- User department to prepare the DQ

- Ensures that the document is in compliance with current policies and procedures of cGMP regulations.

- Ensures that the content is sufficient, clearly defined, technically sound and accurate.

- It is a Guidance document to prepare the DQ.

# 3.2 Review of Document

- To be reviewed by Head of the user department and functional department ( Engineering & Quality assurance)

# 3.3 Approval of Document

- Approval of document by Head Manufacturing/Head Engineering/Head Quality.

# 4.0	Equipment Description & Identification:

# 4.1       Scope:       PSA Nitrogen plant

# 4.2        Purpose:   Purpose of PSA nitrogen plant to generate the Nitrogen through compressed

# air by Pressure swing adsorption (PSA).

# 4.3 Process Equipment Description

# Complete machine can be divided in following sections:

- Compressed air system with filtration.

- Adsorptive air separation.

- Control panel

- Nitrogen storage and supply

4.3.  Compressed air system with filtration:

The required amount of oil/dust free air for the PSA tower plant is delivered at the

PSA tower at the required pressure and temperature.

4.3.2 Adsorptive Air separation:

The adsorptive air separation system shall consist of two CMS adsorption vessel,

Nitrogen buffer pipes, valves and silencer for the exhaust gas. The system shall

produce the required amount of nitrogen at the desired purity on continous basis.

4.3.3 Control panel:

A control panel is deployed housing the starters, sequence programmers and electrical components and devices so as to control the functioning of the PSA nitrogen plant. The panel shall be equipped with required interlocks so as to automate the complete equipment,

4.3.4 Nitrogen storage and supply:

It shall consist of nitrogen storage tank, pressure and flow adjusting meters to store the nitrogen to be used as when required.

# Verified By & Date:

  - USER REQUIREMENTS

  - System Requirements:

| Sr. No. | SYSTEM COMPONENTS | SYSTEM REQUIREMENTS |
| --- | --- | --- |
| 1 | Identification (In case of Equipment /Instrument) | Nitrogen Plant |
| 2 | Model/Type | PSA |
| 3 | Capacity | 5 Nm3/hr. |
| 4 | Potential Suppliers | - Molsieve |
| 5 | Contact parts (In case of Equipment) | SS 316 Pipe line up to user point |
| 6 | Non metallic contact parts (In case of Equipment /Instrument) | - Any material with food grade quality with certificate having no potential impact on the products. 2. Durable. 3. Must be easily cleanable. |
| 10 | Motor & Electrical installations (In case of Equipment /Instrument) | Machine should be operated through mounted on separate electrical control panel. |
| 11 | Machine adjustments (In case of Equipment /Instrument) | Setting with Zero clearance with good accuracy. |
| 12 | Packaging & Transport | Should be packed and transported in such a way to avoid any damage during transportation. |
| 13 | No. of requirements | 01 |
| 14 | Requirements for any power failure backup’s (In case of Equipment /Instrument) | To be backed up by installed in-house DG set. |
| 15 | Method for supply of Compressed air into the equipment | Should be Automatic |
| 16 | Production/Operation stage | Nitrogen |
| 17 | Product nitrogen percentage | Should be 99.99 % |
| 18 | Plant operation | Should be Automatic |
| 19 | Plant Running | Continuous |
| 20 | Plant Mounting | Skid mounted |
| 21 | Plant Location and Available room size | Indoor |

Verified By & Date:

  - Technical Description

| Sr. No. | Specification | SYSTEM REQUIREMENTS |
| --- | --- | --- |
| 1. | Filters | First stage Capacity-35 CFM MOC elements-Borosilicate sintered fiber Make element-Ultra filter Rating-3 microns Second stage Capacity-35CFM MOC element-Borosilicate sintered fiber Make-Ultra filter Rating-0.01 microns |
| 2. | Air Receiver Pressure | Type-Pressure vessel Design code - GEP Design code for fabrication-IS 2825 MOC-IS 2002 Design pressure-9.5 kg/cm2 Design Temperature -55 oC Geometrical Volume 175 liters. Hydraulic test – At 1.4 times the design pressure |
| 3. | PSA Tower | Total Activated Alumina required-40 kg Total CMS required -276 liter. Type- Pressure vessel Design - GEP Design code for fabrication-IS 2825 MOC-IS 2002 Design Pressure -9.5 Kg/cm2 Design Temperature -55 oC Geometrical volume – 188 Lt Hydraulic test – At 1.4 times the design pressure |
| 4. | PSA Module Sliencer | Type-Honeycomb Design Pressure -9.5 Kg/cm2 Design Temperature -55 0C Sound level –Less than 90 DB at 3 meters. |
| 5. | Surge vessel | Type -Pressure vessel Design - GEP Design code for fabrication-IS 2825 MOC-IS 2002 Design Pressure -9.5 Kg/cm2 Design Temperature -55 oC Geometrical volume-800 liters |
| 6. | Control valves for PSA module | Control valves ,On ,OFF type Actuation – Pneumatic, Through a solenoid valve Duty- Robust each valve operated in 1 min. Pressure- should not leak in back pressure of 8 kg/cm2 Medium-Air/nitrogen Design Pressure -9.5 Kg/cm2 Design Temperature -55 oC Pneumatic test- At 1.25 times the design pressure. |
| 7. | Back pressure controller | Type=Pressure holding valve Duty- Robust Medium-Nitrogen Design Pressure -9.5 Kg/cm2 Design Temperature -55 oC Pneumatic test- At 1.25 times the design pressure Set pressure- 5 to 6 kg/cm2 |
| 8. | Flow meter | Type- Velocity based flow meter Tube-Glass/metal Float- SS Range- Should read 5 NM3/hr Design Pressure -9.5 Kg/cm2 Design Temperature -55 oC Pneumatic test- At 1.25 times the design pressure Inlet/outlet - Vertical |
| 9. | Storage vessel | Type -Pressure vessel Design - GEP Design code for fabrication-IS 2825 MOC-IS 2002 Design Pressure -9.5 Kg/cm2 Design Temperature -55 oC Geometrical Volume-2000 liter Hydraulic test – At 1.4 times the design pressure |
| 10. | Carbon molecular sieves | Grade CMS 276 kg |
| 11. | Activated alumina | Grade IPLC 40 kg |

Verified By & Date:

  - Spares :

# a) Change over valves PSA ½ “

# b) Soleniod valve for PSA valve

# c) Auto drain valve

# d) Glass tube for Rotameter

# e) Air filter ½’

# f) FRL ½”

# g) Pressure switch 0-10 Kg/cm2

# h) Pressure switch 0-4 Kg/cm2

# i) Pressure gauge o-10 kg/cm2

Verified By & Date:

  - Detail of components:

| Sr no | Description | Make |
| --- | --- | --- |
| 1 | Carbon molecular sieves | Carbotech,Germany |
| 2 | Change over valves PSA | Airmax SS body |
| 3 | Solenoid valve | Rotex |
| 4 | Pressure switch | Danfoss,Denmark |
| 5 | Pressure gauge | Mass |
| 6 | Pressure regulator | Shavo Nitrogen |
| 7 | Activated Alumina | I.P.C.L Equivalent |
| 8 | Isolation valve | Legris,itlay |
| 9 | Rota meter | I.E.P.L |

# Verified By & Date:

5.5      Utility Details:

| Sr no | Utility | Supply | Requirements |
| --- | --- | --- | --- |
| 1. | # Phase | # 1 Phase & Neutral |  |
| 2. | # Voltage | # 220 V |  |
| 3. | # Frequency | # 50 Hz |  |
| 4. | # Power consumption | # 1 KW |  |
|  | # Compressed air |  |  |
| 1 | # Flow | # 65 Nm3/hr |  |
| 2 | # Pressure | # 7 kg/cm2 |  |

Verified By & Date:

# 5.6    Identification of Component for Calibration

# In the Nitrogen plant, following are the components, which needs calibration. They shall

# be calibrated during/before installation of the equipment at the site:

# Following are the components:

- Pressure gauges.

- Pressure switches

- Safety valve

- Oxygen analyzer sensor

# Verified By & Date:

6.0      COMPLEMENTARY ASPECTS

6.1       Training

| Sr. No. | Specification |  | SYSTEM REQUIREMENTS |
| --- | --- | --- | --- |
| 1 | The vendor Shall supply all available information for the adequate exploitation of equipment. For the Compliance of this purpose at the Job site and/ or at the Vendors Shop. Vendor’s technical staff shall train customer’s personnel. The scope of the Training will be agreed during the contract signature. |  | Yes |
| 2 | The supplier is to include the personnel training activities. The contractor is to specify the foreseen time for: - Operator/Supervisor training - Manager Training - Electrical maintenance training - Mechanical Maintenance training |  | Yes |
| 6.2 Pre Delivery Qualifications (FAT) |  |  |  |
| Sr. No. |  | Specification | SYSTEM REQUIREMENTS |
| 1 |  | The System or its parts as provided for in the scope of supply shall be pre-installed at the vendors shop prior to delivery to customer site. Installation will be completed and documented including mechanical parts as well as electrical connections of all parts to facilitate taking over tests at Vendors shop prior to delivery. | Yes |

6.3 Supplier Technical Documentation Requirements:

| Sr. No. | COMPONENTS | REQUIREMENTS |
| --- | --- | --- |
|  | Technical Documents | FAT,IQ,OQ Electrical Drawing P & ID diagram GA diagram Operation manual Calibration certificates Hydro test certificates Bought out components certificates. MOC certificates |

Verified By & Date:

6.4    Technical Manuals

| Sr. No. | Specification | Requirements |
| --- | --- | --- |
| 1. | Operation Manual-02 copies |  |

Verified By & Date:

7.0 SAFETY AND ENVIRONMENTAL PROTECTION

| Sr No. | Specification | Requirements |
| --- | --- | --- |
| 1 | Environment | NA |
| 7.1 Safety and Interlocking |  |  |
| 1 | Safety valve on air receiver. |  |
| 2 | High pressure switch on air receiver |  |
| 3 | Safety valve on nitrogen surge vessel |  |
| 4 | Oxygen analyser and high oxygen interlock with vent valve |  |
| 5 | High oxygen in the final product |  |
| 6 | Nitrogen storage tank set pressure is achieved. |  |

Verified By & Date:

8.0 CLEANING MAINTENANCE AND SERVICE

| Sr No. | Specification | Requirements |
| --- | --- | --- |
| 1. | In accordance with cGMP guidelines the units must be easy to clean, to disinfect, and where necessary, to sterilize. | YES |
| 2. | The Supplier should guarantee that, if required, a service team can be on site within one working day. | YES |
| 3 | The design should be such as to allow mechanical cleaning of the surface and that the cleanliness of the surface can be checked easily. | YES |
| 4 | All machine parts, in particular instrumentation, should be constructed so that they can be easily removed and calibrated. | YES |
| 5 | All special tools required for running and maintenance should be best. | YES |
| 6 | A spare parts delivery guarantee with in time. | YES |

Verified By & Date:

9.0 RULES AND REGULATION:

These standards, recommendation and requirements are considered the minimum. Specifications that are more stringent or expansive take the precedence. In case of conflict between published requirements, final determination is the responsibility of the Owners Representative

10. SCOPE OF DELIVERY

| Sr No. | Specification | Requirements |
| --- | --- | --- |
| 1. | Units described in the specific system requirements including all necessary controls and instrumentation. | YES |
| 2 | The complete mechanical and electrical installation. | YES |
| 3 | The Connections to all the necessary utilities, exhaust, and waste lines necessary for its operation. | YES |
| 4 | All piping and cabling of the units itself. | YES |
| 5 | Wiring and cable run: all wiring and cable run is part of the supply. Alkem Health Science will supply the main power switches to be located in correspondence to the electrical and control cabinets delivered by the equipment supplier. | YES |
| 6 | All internal contacts of the supplied equipment for the required utilities. | YES |
| 7 | Unload on site of the equipment: the supplier is required to define all the necessary handling devices required to the unloading operation. The supplier will inform at least 4 weeks in advance the day of delivery and the list of required handling devices. | YES |
| 8 | Assembling operation: the required consumable, the internal transportation, the assembling tools and the required personal are part of the supply. | YES |
| 9 | A complete set of commissioning spare parts. | YES |
| 10 | All special tools necessary for use and maintenance of the supplied equipment. | YES |
| 11 | A complete set of two years spare parts should be listed quoted and offered as option. | YES |
| 12 | All test activities as specified in this document. | YES |
| 13 | Training in the use and maintenance of the equipment. | YES |

Verified By & Date:

11.0	 INSTALLATION, COMMISSIONING AND TESTS

11.1    General

| Sr.No. | Specification | Requirements |
| --- | --- | --- |
| 1. | The Contractor must specify for each piece of equipment the Guaranteed performance and the guaranteed system performance. These values will be tested during the acceptance tests. | YES |
| 2 | In addition the functionality described in the user requirements and detailed in the system specifications will be tested. | YES |

11.2 INSTALLATION, COMMISSION

| Sr.No. | Specification | Requirements |
| --- | --- | --- |
| 1 | The commissioning tests will be carried out in accordance with a written test plan developed by the supplier with clearly stated test procedures and acceptance criteria. | YES |
| 2 | The contractor will approve successfully completed tests and will specify items requiring additional work. Representatives from Alkem Health Science. Will attend and participate in the commissioning tests as required. | YES |
| 3 | The installation and commissioning of the system will be performed at the Alkem Health Science. | YES |
| 4 | The commissioning can only start once all the foreseen documents have been delivered by the supplier to Alkem Health Science. | YES |
| 5 | All equipment should be properly installed, adjusted, leveled, tagged, and connected with utilities. | YES |
| 6 | Point to point checks on wiring and pneumatic should be performed. | YES |
| 7 | All instruments should be properly calibrated. | YES |
| 8 | A equipment ( instrument) used for qualification must be listed and approved by Alkem Health Science. | YES |
| 9 | The calibration equipment must have all the necessary documents to demonstrate their maintenance & use. | YES |
| 10 | The last calibration of all this equipment must be less than 6 months old, and evidenced by certificate. | YES |
| 11 | Verification that the interior surfaces of equipment are free of practices and dirt and all points of product contact meet the specified material requirements. | YES |
| 12 | All the clearances and tolerances specified in the drawing or recommended by component manufacturers are correct. | YES |
| 13 | On site verification that valves and other equipment with moving parts are in their normal position if in a power down condition and move in the correct direction with the correct speed and precision. | YES |
| 14 | Verification that all the Input and Output points are connected and labeled according to the documentation and that all the along the input values have been scaled in accordance with the system specification and process requirements. That all equipment components requiring configuration | YES |

11.3 Site Acceptance Test   (SAT)

| Sr. No. | Specification | Requirements |
| --- | --- | --- |
| 1. | This test will be carried out once the commissioning will be completed. The scope will be to verify the performance and the functionality of the system integrated with the other factory systems ( Including sterility testing of at least 02 days). | YES |
| 2 | The test will be carried out to verify the system response with the expected productivity of the system. | YES |
| 3 | Details on the test realization will be defined during the project Phase. The supplier is asked to specify the proposed duration for SAT and the standard procedure proposed. | YES |
| 4 | During SAT the required functionality, performances and system reliability are met. | YES |
| 5 | The Functionality described in the User Requirements Specification and in the System Specifications are verified and met. | YES |
| 6 | All the documentation agreed has been delivered. | YES |

Verified By & Date:

12.0 QUALIFICATION / VALIDATION

| Sr.No. | Specification | Requirements |
| --- | --- | --- |
| 1. | The maintenance Qualification is responsibility of the customer. However, the supplier is responsible for delivering the basic documents for maintenance qualification. | YES |
| 2. | This includes all side costs such as : calibration measuring equipment and instruments: manpower (IQ and OQ will take place completely on Alkem Health Science.) | YES |
| 3 | Time Schedule for IQ/OQ execution will be developed by Alkem Health Science. With the supplier. | YES |
| 4 | Suppliers personnel used for IQ/OQ must be well trained and experienced. This should be documented. | YES |
| 5 | The onsite test run performed by the supplier might become part of the IQ. | YES |
| 6 | Main IQ/OQ steps such as calibration must be performed and documented in accordance to a SOP approved by Alkem Health Science. | YES |
| 7 | All equipment used for qualification must be listed and approved by Alkem Health Science. The calibration equipment should be well documented. | YES |
| 8 | The last Recalibration of all this equipment should be less than 06 month old. Proofed by Certificate. | YES |
| 9 | OQ can only start after IQ approved by Alkem Health Science. | YES |
| 10 | IQ will be carried out by Alkem Health Science. During Installation phase. IQ will include the tests performed by the contractor. | YES |
| 11 | Part of the OQ will be carried out by Alkem Health Science. During commissioning and SAT phase. OQ will include the tests performed by the contractor. | YES |
| 12 | After installation of the equipment at customers site. Complementary IQ & OQ tests will be performed by the Customer and may be supervised by a member of Technical staff. | YES |
| 13 | Qualification documents (In case of equipments/Instruments) | DQ, IQ, OQ |

Verified By & Date:

13.0 GAURANTEE/WARRANTEE

| Sr.No. | Specification | Requirements |
| --- | --- | --- |
| 1. | The System must be warranty including all the sub- system and components for a period of 12 months from the date of the system acceptance for a 03- shift operation. | YES |
| 2 | The servicing companies involved for the Sub- systems maintenance must be declared and the maintenance group organization described. Furthermore, the contractor will be directly responsible of the system assistance and the required operation will be co- ordinate by him. | YES |
| 3 | In case of failures, the intervention will be guaranteed by the contractor within a maximum time limit. The contractor is asked to specify the maximum time limit. | YES |
| 4 | The supplier is asked to propose as option maintenance and assistance contract after the waranty expiration. | YES |

Verified By & Date:

# 14.0 Deviation

# ------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------

# 15.0 Annexure

# ------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------

# 16.0 Summary and Conclusion

# ------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------

# 17.0 Approval of Design Qualification.

| Functional area | Name | Signature | Date |
| --- | --- | --- | --- |
| Head Engineering |  |  |  |
| Head Manufacturing |  |  |  |
| Head Quality |  |  |  |

# 18.    Acceptance By vendor

# Name of Vendor:

# Sign/Date: