# user requirement specification

# name of the item:  PSA nitrogen plant

# functional area:  Beta-Lactam block

# protocol no.:

Alkem LABORATORIES LIMITED (UNIT-II)

village & po: thana, near baddi,

dist.: solan, himachal pradesh

CONTENT

Sr. No.	Description

- URS Approval

- Objective

- Responsibilities

- Equipment Description & Identification

- User Requirements

- Abbreviations

1.0   URS APPROVAL:

Protocol Prepared By:

| Functional area | Name | Signature | Date |
| --- | --- | --- | --- |
| Engineering |  |  |  |

URS Reviewed By:

| Functional area | Name | Signature | Date |
| --- | --- | --- | --- |
| Production |  |  |  |
| Engineering |  |  |  |
| Quality Assurance |  |  |  |

URS Approved By:

| Functional area | Name | Signature | Date |
| --- | --- | --- | --- |
| Head Engineering |  |  |  |
| Head Manufacturing |  |  |  |
| Head Quality |  |  |  |

2.0	Objective:

The purpose of this document is to ensure that all the critical aspects of the equipment, cGMP  & Safety features have been considered in designing the equipment and is properly documented.

3.0      Responsibilities:

In accordance with the document, following  functions shall be responsible for initiation and finalization of equipment user requirement specification. When the work is carried by contract/ consulting staff, all the work is to be performed under the oversight of Alkem labs ltd Unit-II Beta-Lactam Block.

3.1 User Department

- Prepares the User requirement specification document.

- Ensures that the document is in compliance with current policies and procedures of cGMP regulations.

- Ensures that the content is sufficient, clearly defined, technically sound and accurate.

- Distributes the finalized protocol for review and approval signatures.

# 3.2 Production/Validation/Engineering/Quality assurance

- Review of document.

# 3.3 Head Engineering/Head Manufacturing/Head Quality

- Approval of document.

- Verification that the document is complete and properly documented for approval.

# 4.0	Equipment Description & Identification:

  - Scope:

This document covers all aspects of Users requirements for the Equipment / Instrument along with all Attachment, Spare Parts and Accessories to be used in Alkem Labs  Limited, Baddi, Unit-II  Beta-Lactam Block Himachal Pradesh  (India).

Scope incorporates understanding and documentation of critical requirements such as system requirements, cGMP requirements, safety requirements, documentation requirements and operational requirements.

  - Purpose:

Nitrogen purging in Injection filling and Dry syrup filling.

  - USER REQUIREMENTS

  - System Requirements:

| Sr. No. | SYSTEM COMPONENTS | SYSTEM REQUIREMENTS |  |
| --- | --- | --- | --- |
| 01. | Identification (In case of Equipment /Instrument) | PSA nitrogen plant 5 NM3/HR. |  |
| 02. | Model/Type |  |  |
| 03. | Capacity |  |  |
| 04. | Potential Suppliers | 1. |  |
| 05. | Contact parts (In case of Equipment) | SS 316 mirror finish pipe line |  |
| 07. | Non contact parts (In case of Equipment /Instrument) | - MS IS 2002. 2. Durable. 3. Must be easily cleanable. |  |
| 08. | Motor & Electrical installations (In case of Equipment /Instrument) | Machine should be operated on separate electrical control panel. |  |
| 10. | Machine adjustments (In case of Equipment /Instrument) | Setting with Zero clearance with good accuracy. |  |
| 11. | Packaging & Transport | Should be packed and transported in such a way to avoid any damage during transportation. |  |
| 12. | No. of requirements |  |  |
| 13. | Requirements for any power failure backup’s (In case of Equipment /Instrument) | To be backed up by installed in-house DG set. |  |
| 15. | Machine specification |  |  |
| 1. | Compressed air required for generating 5 Nm3/hr |  | 65 Nm3/Hr @7 kg/cm2, oil free and Dust free. |
| 2. | Air Receiver Pressure |  | Pressure vessel Design - GEP pressure -8.5 Kg/cm2 Temperature -55 oC Geometrical Volume 175 liters. |
| 3 | PSA Tower |  | Pressure vessel Design - GEP Pressure -9.5 Kg/cm2 Temperature -55 oC Geometrical volume – 188 Lt |
| 4 | PSA Module Sliencer |  | Honeycomb Pressure -9.5 Kg/cm2 Temperature -55 0C Sound level -90 DB at 3 meters. |
| 5 | Surge vessel |  | Pressure vessel Geometrical volume-800 litres |
| 6. | PSA module |  | Control valves ,On ,OFF type Acuation – Pneumatic, Through a solenoid valve |
| 7. | Back pressure controller |  | Pressure holding valve with Robhust duty. |
| 8. | Flow meter |  | Velocity based flow meter Pressure -9.5 Kg/cm2 |
| 9. | Storage vessel |  | Pressure vessel Volume-2000 liter Operating pressure -4.5 -7.0 Kg/cm2 Temperature -55 0C |
| 10. | Oxygen analyser |  | Range 0-30% Resolution -0.01% Sensor type- Electro chemical |
| 11. | Carbon molecular sieves |  | Grade CMS 276 kg |
| 12 | Activated alumina |  | Grade IPLC 40 kg |
| 13 | Filters |  | 35 CFM,Ultrafilter 3 micron, 0.01 micron. |

  - Product  Acceptance Parameters:

| Sr.no | Specification | Unit | Acceptance Criteria |
| --- | --- | --- | --- |
| 1 | Product nitrogen plant flow rate | Nm3/hr |  |
| 2 | Oxygen in product nitrogen Max | % vol |  |
| 3 | Hydrogen in Product nitrogen | % |  |
| 4 | Physical oil content in product nitrogen max. | Mg/m3 |  |
| 5 | Oil vapour in product nitrogen max | Mg/m3 |  |
| 6 | Product nitrogen+ Argon | % vol |  |
| 7 | Product Nitrogen Temp. | Deg C |  |
| 8 | Product Nitrogen Pressure | Kg/cm2g |  |
| 9 | Suspended particales | Microns |  |
|  | Plant operational Design Parameter |  |  |
| 1 | Plant operation | Automatic |  |
| 2 | Plant Running | Continuous |  |
| 3 | Plant Mounting | Skid Mounted |  |
| 4 | Plant Location | Indoor |  |

5.3	Safety Requirements:

| Sr. No. | SAFETY COMPONENTS | SAFETY REQUIREMENTS |
| --- | --- | --- |
| 01. | Electrical Safety (In case of Equipment /Instrument) | 1. Separate electrical control panel with double earthling provision. 2. Emergency OFF switch. 3. All electrical wires should be given appropriately number and identified and covered with guard. |
| 02. | Mechanical safety (In case of Equipment /Instrument) | 1.No Sharp edges should be present which may result Injury to operating personnel. |
| Sr. No. | SAFETY COMPONENTS | SAFETY REQUIREMENTS |
| 04. | Safety Interlocks (In case of Equipment /Instrument) |  |

  - Documentation Requirements:

| Sr. No. | COMPONENTS | REQUIREMENTS |
| --- | --- | --- |
| 01. | Drawings | 1.Electrical drawing 2.machanical drawing 3.Control panel layout drawing & wiring diagram 4.Instrumentation diagram |
| 02. | Material of Construction Certificates | As per cGMP requirement |
| 03. | Supporting utilities | As per machine requirement |
| 04. | Calibration details | As per cGMP requirement |
| 05. | Documents | Machine manual and qualification documents (DQ, IQ, OQ & PQ) for reference |

  - Operational Requirements:

| Sr. No. | COMPONENTS | REQUIREMENTS |
| --- | --- | --- |
| 06 | Machine manual (If any) | Machine operating and maintenance manual which should comprise of 1. Name, Make , Model No./Type, Sr. No., Mfg date and capacity of the equipment. 2. System Description which includes Machine description as well as Process description. 2. Technical details about all components and their subcomponents. 3. Salient technical features including cGMP features and safety features and alarms if any. 4. Important drawings including Components and sub-component drawings, Electrical diagrams, describing Operating panel component drawings and process Flow chart. 5. MOC for all parts and total surface area of product contact part. 6. Details of Utility requirements and connections. 7. Installation procedures, pre and post installation checklists and details of operational procedures which should also cover all kind of fine adjustments. 8. Calibration requirement for all the instruments. 9. Details about the operating panel and their functions and sequence of operations. 11. Troubleshooting. 12. Changeover procedure if any. 13. Preventive maintenance procedure for developing preventive maintenance SOP. 14. Details about critical bought out items (if any) and their make, model and quantity and if possible backup records / brochures / certificates. 15. Do’s and Don’ts about the machine. 16. Warranty certificate for the equipment and associated accessories. |
| Sr. No. | COMPONENTS | REQUIREMENTS |
| 07. | Qualification documents (In case of equipments/Instruments) | Mandatory: DQ, IQ, OQ & PQ |

| Sr. No. | Operational Critical factor considered | Operational Details |
| --- | --- | --- |
| 01. | Production/Operation stage | Nitrogen generation |
| 02. | Material inputs into the equipment | Compressed air |
| 03. | Desired out come from the equipment | Nitrogen for purging |
| 05. | Method for supply of Comressed air into the equipment | Automatic |
| 06. | Method for Discharging Nitrogen form Storage tank. | Automatic |
| 07. | Expected running time per day |  |
| 08. | Method of cleaning | Manual |
| 09. | Recommended solvent for cleaning with its chemical nature | Clean Duster |
| 10. | Available size of the room for installation | 3200mmX4210mm |

# 6.0	Abbreviation

# SOP      : Standard operating procedure

# S.S.	: Stainless steel

# DQ	: Design Qualification

IQ	: Installation Qualification

OQ	: Operational Qualification

PQ	: Performance Qualification

MOC	: Material of construction

cGMP	: Current Good manufacturing Practices