- Objective

To lay down a procedure for Temperature, Relative Humidity and Differential Pressure Monitoring.

- Scope

This procedure is applicable for Temperature, Relative Humidity and Differential Pressure Monitoring

in Alkem Laboratories Ltd., Unit-II, Baddi.

- Responsibility

Production Technician: To carry out the activity in accordance with the procedure as mentioned in the SOP

Production Officer/ Executive: To ensure that the activity is carried out in accordance with the procedure as mentioned in this SOP.

- Accountability

Head Production

- Procedure

  - Handling Procedure of  Digital Hygrometer

    - Ensure the calibration status of the Digital Hygrometer.

    - Use calibrated Digital Hygrometer for monitoring.

    - Recording procedure of Temperature & Relative Humidity in processing areas

      - Initially Digital Hygrometer shows temperature and % relative humidity of the area.

      - Record the Temperature & Relative Humidity at start of the shift ± 30 min, then every 4 hours ± 30 minutes till completion of the activity or at end of the shift which ever is later.

      - Record the Temperature & Relative Humidity twice in a shift wherever area is not in use. (Start of the shift ± 30 min and at end of the shift)

      - Record the Temperature & Relative Humidity reading as per Annexure I.

    - Recording procedure of Temperature & Relative Humidity in Staging areas.

      - Initially Digital Hygrometer shows temperature and % relative humidity of the area.

      - Record current, minimum and maximum temperature & Relative Humidity of the area as explained below in Annexure II.

      - Press “MODE” button to show minimum humidity and temperature.

      - Press again to “MODE” button to show maximum humidity and temperature.

      - Press again to “MODE” button to monitoring display.

      - After each record press “Set” button to reset the values and to store actual temperature and humidity readings.

      - Record the Temperature & Relative Humidity twice in a shift (Start and at end of the shift).

    - Temperature and RH shall be monitored in the various area of the facility as per Annexure-II.

    - In case of product specific requirement of the environmental conditions, it shall be maintained as per the instructions mentioned in the batch record.

    - If in any area temperature or humidity is not within the limits, inform to engineering department.

    - Engineering department along with Quality Assurance shall investigate the reason for breakdown and decide for action to be taken.

  - Calibration of Hygrometer

    - Hygrometer should be calibrated once in a year by external approved party.

  - Procedure for Pressure difference

    - HVAC in all areas (cubicle and adjacent area) should be started 20 minutes before starting the activity.

    - Ensure that the door of the cubicle and the adjacent area are in closed condition.

    - Before taking the reading at each interval, ensure the cleanliness of SS manometer port. Check and record the ‘Zero’ setting of the manometer by opening the respective door.

    - Read the value on manometer, which is directly corresponding to the indicator needle, if the indicator needle rests in between two divisions on the scale, the average of both readings to be considered.

e.g.   Magnehelic Manometer:

Range: 0 to 20 mm of water gauze

Least count: 02 (value of each division)

    - Record the pressure difference (manometer reading) in processing areas at the Start of the shift ± 30 min, then every 4 hours ± 30 minutes till completion of the activity or at end of the shift which ever is later. Record pressure difference twice in a shift wherever area is not in use (Start of the shift ± 30 min and at end of the shift) as per Annexure –I.

    - Record the pressure difference (manometer reading) in staging area twice in a Shift. (Start and at end of the shift) as per Annexure –II. (wherever Required)

    - If pressure difference is not within limit, stop the activity and inform to QA and Engineering department.

    - Engineering department along with QA should investigate the reason for deviation in pressure difference and rectify the same. In case of any major breakdown, QA should decide line of action.

    - Magnehelic Manometer should be calibrated once in a year by external approved party.

- Annexure (S)

Annexure – I		:  Temperature, Relative Humidity and Differential Pressure Record.

Annexure – II	:  Temperature, Relative Humidity and Differential Pressure Record.

(Staging Area)

- Reference (S)

NA

- Glossary

SOP		:	Standard Operating Procedure

NO		:	Number

S.S		:	Stainless Steel

- Revision History

| Revision No. | Details Of Changes | Reason for Change |
| --- | --- | --- |
| 00 | New SOP | NA |