- Revision History

| Rev.No. | Details of changes | Reason for change |
| --- | --- | --- |
| 01 | NA | Periodic Review |
| 02 | Increase hold time study of freshly prepared 70% IPA | Due to change hold time study from 24 hours to 72 hours of freshly prepared 70% IPA. |

2.0    Objective

To lay down a procedure for handling of sterile raw material during power failure.

# 3.0    Scopes

This SOP is applicable for the handling of sterile raw material during power failure in C Block.

# 4.0   Responsibility

Officer and Above Production	:	Implementation of Procedure.

5.0   Accountability

Production Head.

6.0    Procedure

6.1	  Prestart Up

6.1.1 Ensure the LAF is in working condition and differential pressure within the specified limit (8 to 15 mm of WC).

6.1.2 Ensure the raw material containers are placed under LAF with lid closed.

6.1.3 Ensure the temperature and humidity of the room is within the specified limit as per    product requirement.

    - Ensure during power failure the movement in the room should be limited to unavoidable type.

6.2      Operation

- During power failure monitor the LAF over vial filling and sealing machines in operational condition as the LAF unit is connected with UPS.

- Keep always the lid of the hoppers of vial filling machine in closed condition.

- After resumption of power connections wait for five minutes and allow the area to get stabilized and spray 70% IPA solution before start of the operation.

- Start the filling operation after checking the temperature, humidity and differential pressure             of aseptic area.

- Mop the remaining container of RM from outside with the help of lint free mop using freshly prepared 70% IPA solution (use within 72 hrs) thoroughly.

- Continue the filling operation till all the batch raw material used.

NOTE: In case the power failure continues for half an hour then discontinue aseptic filling operation. Cleaning and sanitization of aseptic area shall be done as per SOP No. PC/057.

7.0      Annexure (S)

NA

8.0     Reference (S)

SOP NO. - PC/057.

9.0     Glossary

SOP   	: Standard Operating Procedure.

LAF		: Laminar air flow.

IPA		: Isopropyl Alcohol

UPS		: Uninterrupted power supply.

PC		: Production C-Block.

No.		: Number.