- Revision History

| Rev.No. | Details of changes | Reason for change |
| --- | --- | --- |
| 01 | NA | Periodic Review |
| 02 | Specification of the magnehelic gauge limit of LAF. | Due to magnehelic gauge limit of LAF was not Specified in old SOP’s |

2.0    Objective

To lay down a procedure for starting of vial filling after a break.

3.0    Scopes

This SOP is applicable for the vial-filling after a break of C Block.

4.0	   Responsibility

Officer and Above Production/ IPQA officer	:	Implementation of Procedure.

5.0	 Accountability

Production Head.

6.0    Procedure

6.1    Prestart Up

6.1.1 Ensure that the AHU of aseptic area is in working condition and all the differential pressure readings are with in specified limit.

    - Ensure the cleaning of aseptic area done as per SOP No. PC/057.

6.1.3   Ensure the temperature and humidity of the aseptic area is with in specified limit as per product requirement.

6.1.4	Ensure the viable and non-viable count of aseptic area is performed as per SOP. QC/138 and QC/064.

6.1.5	Ensure all the LAF units are in working condition and all the differential pressure readings are within specified limits (8 to 15 mm of wc) and mobile LAF is also functioning during power shut down and differential pressure readings is within specified limit (8 to 15 mm of wc).

  - Operation

6.2.1   Before starting any operation in the area after a break check the microbial count by settle plate as well as by dynamic air sampling.

6.2.2    Non-viable count of the area to be checked at rest and in dynamic condition for NLT two days.

6.2.3   Cleaning of the area should be done daily as per the schedule using filtered disinfectant solution as per schedule.

6.2.4   If plate count report of the area is satisfactory then planning for vial filling to be taken.

6.2.5  After getting line clearance from QA Start processing the primary packing material for sterilization as the material get sterilized unload the component in aseptic area for processing.

7.0       Annexure (S)

NA

8.0       Reference (S)

SOP No. PC/057

QC/138

QC/064

9.0	Glossary

SOP   	: Standard Operating Procedure.

LAF	: Laminar air flow.

AHU	: Air Handling Unit

NO.      : Number

QA	: Quality Assurance

PC	: Production (C-Block)

QC	: Quality Control

NLT	: Not Less Than